## Summary
|  | O1 | A3 | A4 | h48 | g19 | D15 | D20
Heating and Air Conditioning | [5 empty] | AC Cost
| SF NC Gas Z3 | Single Family: New Construction | Gas Option | 3 | 5962 |  | Ducted attic furnace 80 AFUE, 40 kBtu/h | No AC
| SF NC Electric Z3 S | Single Family: New Construction | Electric Option | 3 | 10036 |  | Heating included in split system heat pump | Ducted Split Heat Pump AHU in attic, 2 ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF NC Electric Z3 O1 | Single Family: New Construction | Electric Option | 3 | 9683 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 2-ton 14 SEER/12.2 EER, 8.2 HSPF, single speed
| SF NC Electric Z3 O2 | Single Family: New Construction | Electric Option | 3 | 12041 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 2-ton 21 SEER/15 EER, 13 HSPF, variable-speed
| SF NC Gas Z4 | Single Family: New Construction | Gas Option | 4 | 13267 |  | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2.5 tons
| SF NC Electric Z4 | Single Family: New Construction | Electric Option | 4 | 10415 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 2.5-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF NC Gas Z6 | Single Family: New Construction | Gas Option | 6 | 12132 |  | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2 tons
| SF NC Electric Z6 | Single Family: New Construction | Electric Option | 6 | 9492 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 2-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF NC Gas Z9 | Single Family: New Construction | Gas Option | 9 | 12706 |  | Ducted attic furnace 80 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 2.5 tons
| SF NC Electric Z9 | Single Family: New Construction | Electric Option | 9 | 10181 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF NC Gas Z10 | Single Family: New Construction | Gas Option | 10 | 11880 |  | Ducted attic furnace 80 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 3 tons
| SF NC Electric Z10 | Single Family: New Construction | Electric Option | 10 | 9768 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF NC Gas Z12 | Single Family: New Construction | Gas Option | 12 | 11604 |  | Ducted attic furnace 80 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 3 tons
| SF NC Electric Z12 | Single Family: New Construction | Electric Option | 12 | 9630 |  | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 90 Gas Z3 | Single Family: 1990's | Gas Option | 3 | 18468 | 3500 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2 tons
| SF 90 Electric Z3 S | Single Family: 1990's | Electric Option | 3 | 17061 | 5400 | Heating included in split system heat pump | Ducted split heat pump, fan coil in-unit, 3-ton 21 SEER/13 EER, 11 HSPF, two speed
| SF 90 Electric Z3 O1 | Single Family: 1990's | Electric Option | 3 | 16772 | 5200 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 3-ton 14 SEER/12.2 EER, 8.2 HSPF, single speed
| SF 90 Electric Z3 O2 | Single Family: 1990's | Electric Option | 3 | 17985 | 6800 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 3-ton 21 SEER/15 EER, 13 HSPF, variable-speed
| SF 90 Gas Z4 | Single Family: 1990's | Gas Option | 4 | 18656 | 4500 | Ducted attic furnace 80 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 4 tons
| SF 90 Electric Z4 | Single Family: 1990's | Electric Option | 4 | 15262 | 5400 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 90 Gas Z6 | Single Family: 1990's | Gas Option | 6 | 15958 | 4200 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 3 tons
| SF 90 Electric Z6 | Single Family: 1990's | Electric Option | 6 | 13979 | 5400 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 90 Gas Z9 | Single Family: 1990's | Gas Option | 9 | 16931 | 4500 | Ducted attic furnace 80 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 4 tons
| SF 90 Electric Z9 | Single Family: 1990's | Electric Option | 9 | 14632 | 5900 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 90 Gas Z10 | Single Family: 1990's | Gas Option | 10 | 16932 | 5200 | Ducted attic furnace 80 AFUE, 90 kBtu/h | Split AC 14 SEER/12.2 EER, 5 tons
| SF 90 Electric Z10 | Single Family: 1990's | Electric Option | 10 | 13910 | 6100 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 90 Gas Z12 | Single Family: 1990's | Gas Option | 12 | 16317 | 5200 | Ducted attic furnace 80 AFUE, 80 kBtu/h | Split AC 14 SEER/12.2 EER, 5 tons
| SF 90 Electric Z12 | Single Family: 1990's | Electric Option | 12 | 13679 | 6100 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 78 Gas Z3 | Single Family: Pre-1978 | Gas Option | 3 | 25331 | 3500 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2 tons
| SF 78 Electric Z3 S | Single Family: Pre-1978 | Electric Option | 3 | 20633 | 7600 | Heating included in split system heat pump | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 21 SEER/13 EER, 11 HSPF
| SF 78 Electric Z3 O1 | Single Family: Pre-1978 | Electric Option | 3 | 20056 | 7200 | Heating included in split system heat pump | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 14 SEER/12.2 EER, 8.2 HSPF
| SF 78 Electric Z3 O2 | Single Family: Pre-1978 | Electric Option | 3 | 23376 | 9500 | Heating included in split system heat pump | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 30 SEER/15 EER, 14 HSPF
| SF 78 Gas Z4 | Single Family: Pre-1978 | Gas Option | 4 | 24225 | 3500 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2 tons
| SF 78 Electric Z4 | Single Family: Pre-1978 | Electric Option | 4 | 20278 | 8000 | Heating included in split system heat pump | Non-ducted mini-split heat pump, 3 indoor units, 4-ton 21 SEER/13 EER, 11 HSPF
| SF 78 Gas Z6 | Single Family: Pre-1978 | Gas Option | 6 | 22603 | 4200 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 3 tons
| SF 78 Electric Z6 | Single Family: Pre-1978 | Electric Option | 6 | 18205 | 7600 | Heating included in split system heat pump | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 21 SEER/13 EER, 11 HSPF
| SF 78 Gas Z9 | Single Family: Pre-1978 | Gas Option | 9 | 22994 | 4500 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 4 tons
| SF 78 Electric Z9 | Single Family: Pre-1978 | Electric Option | 9 | 18879 | 8000 | Heating included in split system heat pump | Non-ducted mini-split heat pump, 3 indoor units, 4-ton 21 SEER/13 EER, 11 HSPF
| SF 78 Gas Z10 | Single Family: Pre-1978 | Gas Option | 10 | 17643 | 5200 | Ducted attic furnace 80 AFUE, 90 kBtu/h | Split AC 14 SEER/12.2 EER, 5 tons
| SF 78 Electric Z10 | Single Family: Pre-1978 | Electric Option | 10 | 15651 | 6100 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed
| SF 78 Gas Z12 | Single Family: Pre-1978 | Gas Option | 12 | 16593 | 5200 | Ducted attic furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 5 tons
| SF 78 Electric Z12 | Single Family: Pre-1978 | Electric Option | 12 | 15370 | 6100 | Heating included in split system heat pump | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed

## Sheet1
Zone |  | Labor | OH&P | Design | Test & Inspect | Market
3 | San Francisco | 95 | 20% | 10% | 1.25% | 8%
4 | San Jose | 95 | 18% | 10% | 1.25% | 5%
6 | Santa Barbara / Santa Monica / Long Beach | 85 | 15% | 10% | 1.25% | 2%
9 | Pasadena / Burbank / Pomona | 85 | 15% | 10% | 1.25% | 2%
10 | Riverside / San Bernadino | 70 | 15% | 10% | 1.25% | 0%
12 | Sacramento | 65 | 15% | 10% | 1.25% | 0%

## SF NC Gas Z3
Single Family | [8 empty] | Single Family: New Construction
New Construction
Gas Option
3
Demolition
|  | Remove existing furnace |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | None
New Air Conditioner, equipment price
No AC
Concrete pad, precast
Refrigerant piping and refrigerant
Miscellaneous supplies
Labor
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 75 | 75
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping | 30 | LF | 3 | 90
|  |  | Labor | 16 | HR | 95 | 1520
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
5055
|  | Subtotal |  |  |  |  | 5055
0
| General Conditions and Overhead |  |  | 12% |  |  | 607 | 0
| Design and Engineering |  |  | 4% |  |  | 226 | 0
| Permit, testing and inspection |  |  | 1.25% |  |  | 74 | 0
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 5962

## SF NC Gas Z4
Single Family | [8 empty] | Single Family: New Construction
New Construction
Gas Option
4
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3800 | 3800
|  |  | Split AC 14 SEER/12.2 EER, 2.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 75 | 150
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 30 | LF | 3 | 90
|  |  | Labor | 16 | HR | 95 | 1520
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
11350
|  | Subtotal |  |  |  |  | 11350
0
| General Conditions and Overhead |  |  | 11% |  |  | 1249 | 0
| Design and Engineering |  |  | 4% |  |  | 504
| Permit, testing and inspection |  |  | 1.25% |  |  | 164
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 13267

## SF NC Gas Z6
Single Family | [8 empty] | Single Family: New Construction
New Construction
Gas Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3500 | 3500
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 75 | 150
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 30 | LF | 3 | 90
|  |  | Labor | 16 | HR | 85 | 1360
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
10570
|  | Subtotal |  |  |  |  | 10570
0
| General Conditions and Overhead |  |  | 9% |  |  | 951 | 0
| Design and Engineering |  |  | 4% |  |  | 461
| Permit, testing and inspection |  |  | 1.25% |  |  | 150
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 12132

## SF NC Gas Z9
Single Family | [8 empty] | Single Family: New Construction
New Construction
Gas Option
9
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1400 | 1400
|  |  | Ducted attic furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3800 | 3800
|  |  | Split AC 14 SEER/12.2 EER, 2.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 75 | 150
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 30 | LF | 3 | 90
|  |  | Labor | 16 | HR | 85 | 1360
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
11070
|  | Subtotal |  |  |  |  | 11070
0
| General Conditions and Overhead |  |  | 9% |  |  | 996 | 0
| Design and Engineering |  |  | 4% |  |  | 483
| Permit, testing and inspection |  |  | 1.25% |  |  | 157
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 12706

## SF NC Gas Z10
Single Family | [8 empty] | Single Family: New Construction
New Construction
Gas Option
10
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1400 | 1400
|  |  | Ducted attic furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 70 | 1120
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3800 | 3800
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 70 | 1120
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 75 | 150
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 30 | LF | 3 | 90
|  |  | Labor | 16 | HR | 70 | 1120
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
10350
|  | Subtotal |  |  |  |  | 10350
0
| General Conditions and Overhead |  |  | 9% |  |  | 932 | 0
| Design and Engineering |  |  | 4% |  |  | 451
| Permit, testing and inspection |  |  | 1.25% |  |  | 147
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 11880

## SF NC Gas Z12
Single Family | [8 empty] | Single Family: New Construction
New Construction
Gas Option
12
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1400 | 1400
|  |  | Ducted attic furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 65 | 1040
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3800 | 3800
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 65 | 1040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 75 | 150
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 30 | LF | 3 | 90
|  |  | Labor | 16 | HR | 65 | 1040
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
10110
|  | Subtotal |  |  |  |  | 10110
0
| General Conditions and Overhead |  |  | 9% |  |  | 910 | 0
| Design and Engineering |  |  | 4% |  |  | 441
| Permit, testing and inspection |  |  | 1.25% |  |  | 143
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 11604

## SF 90 Gas Z3
Single Family | [8 empty] | Single Family: 1990's
1990's
Gas Option
3
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3500 | 3500
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 8 | HR | 95 | 760
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 4 | HR | 95 | 380
11535
|  | Subtotal |  |  |  |  | 12795
0
| General Conditions and Overhead |  |  | 20% |  |  | 2559 | 0
| Design and Engineering |  |  | 10% |  |  | 1535
| Permit, testing and inspection |  |  | 1.25% |  |  | 211
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1368
0
| Recommended Budget | [5 empty] | 18468
0

## SF 90 Gas Z4
Single Family | [8 empty] | Single Family: 1990's
1990's
Gas Option
4
Demolition
Remove existing furnace & air conditioner
|  |  | Labor | 12 | HR | 95 | 1140
|  |  | Disposal | 1 | LS | 500 | 500
1640
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1400 | 1400
|  |  | Ducted attic furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4500 | 4500
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment |  |  |  | Not required
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 8 | HR | 95 | 760
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 4 | HR | 95 | 380
11880
|  | Subtotal |  |  |  |  | 13520
0
| General Conditions and Overhead |  |  | 18% |  |  | 2434 | 0
| Design and Engineering |  |  | 10% |  |  | 1595
| Permit, testing and inspection |  |  | 1.25% |  |  | 219
| Contractor Profit/Market Factor |  |  | 5% |  |  | 888
| Recommended Budget | [5 empty] | 18656

## SF 90 Gas Z6
Single Family | [8 empty] | Single Family: 1990's
1990's
Gas Option
6
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4200 | 4200
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 8 | HR | 85 | 680
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 4 | HR | 85 | 340
11035
|  | Subtotal |  |  |  |  | 12215
0
| General Conditions and Overhead |  |  | 15% |  |  | 1832 | 0
| Design and Engineering |  |  | 10% |  |  | 1405
| Permit, testing and inspection |  |  | 1.25% |  |  | 193
| Contractor Profit/Market Factor |  |  | 2% |  |  | 313
0
| Recommended Budget | [5 empty] | 15958
0

## SF 90 Gas Z9
Single Family | [8 empty] | Single Family: 1990's
1990's
Gas Option
9
Demolition
Remove existing furnace
|  |  | Labor | 12 | HR | 85 | 1020
|  |  | Disposal | 1 | LS | 500 | 500
1520
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1400 | 1400
|  |  | Ducted attic furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4500 | 4500
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment |  |  |  | Not required
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 8 | HR | 85 | 680
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 4 | HR | 85 | 340
11440
|  | Subtotal |  |  |  |  | 12960
0
| General Conditions and Overhead |  |  | 15% |  |  | 1944 | 0
| Design and Engineering |  |  | 10% |  |  | 1490
| Permit, testing and inspection |  |  | 1.25% |  |  | 205
| Contractor Profit/Market Factor |  |  | 2% |  |  | 332
| Recommended Budget | [5 empty] | 16931

## SF 90 Gas Z10
Single Family | [8 empty] | Single Family: 1990's
1990's
Gas Option
10
Demolition
Remove existing furnace
|  |  | Labor | 12 | HR | 70 | 840
|  |  | Disposal | 1 | LS | 500 | 500
1340
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1800 | 1800
|  |  | Ducted attic furnace 80 AFUE, 90 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 70 | 1120
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5200 | 5200
|  |  | Split AC 14 SEER/12.2 EER, 5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 70 | 1120
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment |  |  |  | Not required
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 8 | HR | 70 | 560
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 4 | HR | 70 | 280
11880
|  | Subtotal |  |  |  |  | 13220
0
| General Conditions and Overhead |  |  | 15% |  |  | 1983 | 0
| Design and Engineering |  |  | 10% |  |  | 1520
| Permit, testing and inspection |  |  | 1.25% |  |  | 209
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 16932

## SF 90 Gas Z12
Single Family | [8 empty] | Single Family: 1990's
1990's
Gas Option
12
Demolition
Remove existing furnace
|  |  | Labor | 12 | HR | 65 | 780
|  |  | Disposal | 1 | LS | 500 | 500
1280
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1600 | 1600
|  |  | Ducted attic furnace 80 AFUE, 80 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 65 | 1040
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5200 | 5200
|  |  | Split AC 14 SEER/12.2 EER, 5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 65 | 1040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment |  |  |  | Not required
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 8 | HR | 65 | 520
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 4 | HR | 65 | 260
11460
|  | Subtotal |  |  |  |  | 12740
0
| General Conditions and Overhead |  |  | 15% |  |  | 1911 | 0
| Design and Engineering |  |  | 10% |  |  | 1465
| Permit, testing and inspection |  |  | 1.25% |  |  | 201
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 16317

## SF 78 Gas Z3
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Gas Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3500 | 3500
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 16 | HR | 95 | 1520
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork | 100 | LB | 3 | 300
|  |  | Wall/Ceiling patch | 1 | LS | 500 | 500
|  |  | Labor | 40 | HR | 95 | 3800
16305
|  | Subtotal |  |  |  |  | 17565
0
| General Conditions and Overhead |  |  | 20% |  |  | 3513 | 0
| Design and Engineering |  |  | 10% |  |  | 2108
Permit, testing and inspection
|  |  |  | 8% |  |  | 1855
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 290
| Recommended Budget | [5 empty] | 25331

## SF 78 Gas Z4
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Gas Option
4
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 3500 | 3500
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 16 | HR | 95 | 1520
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork | 100 | LB | 3 | 300
|  |  | Wall/Ceiling patch | 1 | LS | 500 | 500
|  |  | Labor | 40 | HR | 95 | 3800
16305
|  | Subtotal |  |  |  |  | 17565
0
| General Conditions and Overhead |  |  | 18% |  |  | 3162 | 0
| Design and Engineering |  |  | 10% |  |  | 2073
Permit, testing and inspection
|  |  |  | 5% |  |  | 1140
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 285
| Recommended Budget | [5 empty] | 24225

## SF 78 Gas Z6
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Gas Option
6
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4200 | 4200
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 16 | HR | 85 | 1360
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork | 100 | LB | 3 | 300
|  |  | Wall/Ceiling patch | 1 | LS | 500 | 500
|  |  | Labor | 40 | HR | 85 | 3400
16125
|  | Subtotal |  |  |  |  | 17305
0
| General Conditions and Overhead |  |  | 15% |  |  | 2596 | 0
| Design and Engineering |  |  | 10% |  |  | 1990
Permit, testing and inspection
|  |  |  | 2% |  |  | 438
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 274
| Recommended Budget | [5 empty] | 22603

## SF 78 Gas Z9
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Gas Option
9
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4500 | 4500
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 16 | HR | 85 | 1360
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork | 100 | LB | 3 | 300
|  |  | Wall/Ceiling patch | 1 | LS | 500 | 500
|  |  | Labor | 40 | HR | 85 | 3400
16425
|  | Subtotal |  |  |  |  | 17605
0
| General Conditions and Overhead |  |  | 15% |  |  | 2641 | 0
| Design and Engineering |  |  | 10% |  |  | 2025
Permit, testing and inspection
|  |  |  | 2% |  |  | 445
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 278
| Recommended Budget | [5 empty] | 22994

## SF 78 Gas Z10
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Gas Option
10
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 70 | 560
|  |  | Disposal | 1 | LS | 500 | 500
1060
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1700 | 1700
|  |  | Ducted attic furnace 80 AFUE, 90 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 70 | 1120
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5200 | 5200 | * Used to be 2-ton system at $3,500/unit
|  |  | Split AC 14 SEER/12.2 EER, 5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 70 | 1120
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification | 1 | EA |  | 0 | * Previously $800, updated per email with Peter Morris 9/25/2018
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 16 | HR | 70 | 1120
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 70 | 560
12715
|  | Subtotal |  |  |  |  | 13775
0
| General Conditions and Overhead |  |  | 15% |  |  | 2066 | 0
| Design and Engineering |  |  | 10% |  |  | 1584
| Permit, testing and inspection |  |  | 1.25% |  |  | 218
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 17643

## SF 78 Gas Z12
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Gas Option
12
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 65 | 520
|  |  | Disposal | 1 | LS | 500 | 500
1020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 1200 | 1200
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 65 | 1040
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5200 | 5200 | * Used to be 2-ton system at $3,500/unit
|  |  | Split AC 14 SEER/12.2 EER, 5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 65 | 1040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 1 | EA | 95 | 95
|  |  | Panel and main service modification | 1 | EA |  | 0 | * Previously $800, updated per email with Peter Morris 9/25/2018
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 16 | HR | 65 | 1040
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 65 | 520
11935
|  | Subtotal |  |  |  |  | 12955
0
| General Conditions and Overhead |  |  | 15% |  |  | 1943 | 0
| Design and Engineering |  |  | 10% |  |  | 1490
| Permit, testing and inspection |  |  | 1.25% |  |  | 205
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 16593

## SF NC Electric Z3 S
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4800 | 4800
|  |  | Ducted Split Heat Pump AHU in attic, 2 ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 95 | 760
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8510
|  | Subtotal |  |  |  |  | 8510
0
| General Conditions and Overhead |  |  | 12% |  |  | 1021 | 0
| Design and Engineering |  |  | 4% |  |  | 381
| Permit, testing and inspection |  |  | 1.25% |  |  | 124
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 10036

## SF NC Electric Z3 O1
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4500 | 4500
|  |  | Ducted split heat pump AHU in attic, 2-ton 14 SEER/12.2 EER, 8.2 HSPF, single speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 95 | 760
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8210
|  | Subtotal |  |  |  |  | 8210
0
| General Conditions and Overhead |  |  | 12% |  |  | 985 | 0
| Design and Engineering |  |  | 4% |  |  | 368
| Permit, testing and inspection |  |  | 1.25% |  |  | 120
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 9683

## SF NC Electric Z3 O2
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 6500 | 6500
|  |  | Ducted split heat pump AHU in attic, 2-ton 21 SEER/15 EER, 13 HSPF, variable-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 95 | 760
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
10210
|  | Subtotal |  |  |  |  | 10210
0
| General Conditions and Overhead |  |  | 12% |  |  | 1225 | 0
| Design and Engineering |  |  | 4% |  |  | 457
| Permit, testing and inspection |  |  | 1.25% |  |  | 149
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 12041

## SF NC Electric Z4
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
4
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5200 | 5200
|  |  | Ducted split heat pump AHU in attic, 2.5-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 95 | 760
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8910
|  | Subtotal |  |  |  |  | 8910
0
| General Conditions and Overhead |  |  | 11% |  |  | 980 | 0
| Design and Engineering |  |  | 4% |  |  | 396
| Permit, testing and inspection |  |  | 1.25% |  |  | 129
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 10415

## SF NC Electric Z6
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 4800 | 4800
|  |  | Ducted split heat pump AHU in attic, 2-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 85 | 680
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8270
|  | Subtotal |  |  |  |  | 8270
0
| General Conditions and Overhead |  |  | 9% |  |  | 744 | 0
| Design and Engineering |  |  | 4% |  |  | 361
| Permit, testing and inspection |  |  | 1.25% |  |  | 117
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 9492

## SF NC Electric Z9
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
9
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5400 | 5400
|  |  | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 85 | 680
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8870
|  | Subtotal |  |  |  |  | 8870
0
| General Conditions and Overhead |  |  | 9% |  |  | 798 | 0
| Design and Engineering |  |  | 4% |  |  | 387
| Permit, testing and inspection |  |  | 1.25% |  |  | 126
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 10181

## SF NC Electric Z10
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
10
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5400 | 5400
|  |  | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 70 | 1120
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 70 | 560
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8510
|  | Subtotal |  |  |  |  | 8510
0
| General Conditions and Overhead |  |  | 9% |  |  | 766 | 0
| Design and Engineering |  |  | 4% |  |  | 371
| Permit, testing and inspection |  |  | 1.25% |  |  | 121
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 9768

## SF NC Electric Z12
Single Family | [8 empty] | Single Family: New Construction
New Construction
Electric Option
12
Demolition
|  | Remove existing furnace |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5400 | 5400
|  |  | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 65 | 1040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 65 | 130
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 8 | HR | 65 | 520
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
8390
|  | Subtotal |  |  |  |  | 8390
0
| General Conditions and Overhead |  |  | 9% |  |  | 755 | 0
| Design and Engineering |  |  | 4% |  |  | 366
| Permit, testing and inspection |  |  | 1.25% |  |  | 119
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 9630

## SF 90 Electric Z3 S
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5400 | 5400 | * Updated per email with Peter Morris 9/25/2018
|  |  | Ducted split heat pump, fan coil in-unit, 3-ton 21 SEER/13 EER, 11 HSPF, two speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 12 | HR | 95 | 1140
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 95 | 760
10560
|  | Subtotal |  |  |  |  | 11820
0
| General Conditions and Overhead |  |  | 20% |  |  | 2364 | 0
| Design and Engineering |  |  | 10% |  |  | 1418
| Permit, testing and inspection |  |  | 1.25% |  |  | 195
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1264
| Recommended Budget | [5 empty] | 17061

## SF 90 Electric Z3 O1
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5200 | 5200
|  |  | Ducted split heat pump AHU in attic, 3-ton 14 SEER/12.2 EER, 8.2 HSPF, single speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 12 | HR | 95 | 1140
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 95 | 760
10360
|  | Subtotal |  |  |  |  | 11620
0
| General Conditions and Overhead |  |  | 20% |  |  | 2324 | 0
| Design and Engineering |  |  | 10% |  |  | 1394
| Permit, testing and inspection |  |  | 1.25% |  |  | 192
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1242
| Recommended Budget | [5 empty] | 16772

## SF 90 Electric Z3 O2
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 6800 | 6800
|  |  | Ducted split heat pump AHU in attic, 3-ton 21 SEER/15 EER, 13 HSPF, variable-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 4 | HR | 95 | 380
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 95 | 760
11200
|  | Subtotal |  |  |  |  | 12460
0
| General Conditions and Overhead |  |  | 20% |  |  | 2492 | 0
| Design and Engineering |  |  | 10% |  |  | 1495
| Permit, testing and inspection |  |  | 1.25% |  |  | 206
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1332
| Recommended Budget | [5 empty] | 17985

## SF 90 Electric Z4
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
4
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5400 | 5400
|  |  | Ducted split heat pump AHU in attic, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 4 | HR | 95 | 380
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 95 | 760
9800
|  | Subtotal |  |  |  |  | 11060
0
| General Conditions and Overhead |  |  | 18% |  |  | 1991 | 0
| Design and Engineering |  |  | 10% |  |  | 1305
| Permit, testing and inspection |  |  | 1.25% |  |  | 179
| Contractor Profit/Market Factor |  |  | 5% |  |  | 727
| Recommended Budget | [5 empty] | 15262

## SF 90 Electric Z6
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
6
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5400 | 5400
|  |  | Ducted split heat pump AHU in attic, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 4 | HR | 85 | 340
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 85 | 680
9520
|  | Subtotal |  |  |  |  | 10700
0
| General Conditions and Overhead |  |  | 15% |  |  | 1605 | 0
| Design and Engineering |  |  | 10% |  |  | 1231
| Permit, testing and inspection |  |  | 1.25% |  |  | 169
| Contractor Profit/Market Factor |  |  | 2% |  |  | 274
| Recommended Budget | [5 empty] | 13979

## SF 90 Electric Z9
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
9
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 5900 | 5900
|  |  | Ducted split heat pump AHU in attic, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 4 | HR | 85 | 340
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 85 | 680
10020
|  | Subtotal |  |  |  |  | 11200
0
| General Conditions and Overhead |  |  | 15% |  |  | 1680 | 0
| Design and Engineering |  |  | 10% |  |  | 1288
| Permit, testing and inspection |  |  | 1.25% |  |  | 177
| Contractor Profit/Market Factor |  |  | 2% |  |  | 287
| Recommended Budget | [5 empty] | 14632

## SF 90 Electric Z10
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
10
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 70 | 560
|  |  | Disposal | 1 | LS | 500 | 500
1060
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 6100 | 6100
|  |  | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 70 | 1120
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 4 | HR | 70 | 280
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 70 | 560
9800
|  | Subtotal |  |  |  |  | 10860
0
| General Conditions and Overhead |  |  | 15% |  |  | 1629 | 0
| Design and Engineering |  |  | 10% |  |  | 1249
| Permit, testing and inspection |  |  | 1.25% |  |  | 172
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 13910

## SF 90 Electric Z12
Single Family | [8 empty] | Single Family: 1990's
1990's
Electric Option
12
Demolition
Remove existing furnace
|  |  | Labor | 8 | HR | 65 | 520
|  |  | Disposal | 1 | LS | 500 | 500
1020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 6100 | 6100
|  |  | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 65 | 1040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 4 | HR | 65 | 260
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 65 | 520
9660
|  | Subtotal |  |  |  |  | 10680
0
| General Conditions and Overhead |  |  | 15% |  |  | 1602 | 0
| Design and Engineering |  |  | 10% |  |  | 1228
| Permit, testing and inspection |  |  | 1.25% |  |  | 169
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 13679

## SF 78 Electric Z3 S
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 7600 | 7600
|  |  | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 3 | EA | 200 | 600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 5 | EA | 95 | 475
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 95 | 1140
|  | Ductwork modifications |  |  |  |  | None
Miscellaneous supplies
Labor
13035
|  | Subtotal |  |  |  |  | 14295
0
| General Conditions and Overhead |  |  | 20% |  |  | 2859 | 0
| Design and Engineering |  |  | 10% |  |  | 1715
| Permit, testing and inspection |  |  | 1.25% |  |  | 236
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1528
| Recommended Budget | [5 empty] | 20633

## SF 78 Electric Z3 O1
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 7200 | 7200
|  |  | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 14 SEER/12.2 EER, 8.2 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 3 | EA | 200 | 600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 5 | EA | 95 | 475
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 95 | 1140
|  | Ductwork modifications |  |  |  |  | None
Miscellaneous supplies
Labor
12635
|  | Subtotal |  |  |  |  | 13895
0
| General Conditions and Overhead |  |  | 20% |  |  | 2779 | 0
| Design and Engineering |  |  | 10% |  |  | 1667
| Permit, testing and inspection |  |  | 1.25% |  |  | 229
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1486
| Recommended Budget | [5 empty] | 20056

## SF 78 Electric Z3 O2
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 9500 | 9500
|  |  | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 3 | EA | 200 | 600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 5 | EA | 95 | 475
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 95 | 1140
|  | Ductwork modifications |  |  |  |  | None
Miscellaneous supplies
Labor
14935
|  | Subtotal |  |  |  |  | 16195
0
| General Conditions and Overhead |  |  | 20% |  |  | 3239 | 0
| Design and Engineering |  |  | 10% |  |  | 1943
| Permit, testing and inspection |  |  | 1.25% |  |  | 267
| Contractor Profit/Market Factor |  |  | 8% |  |  | 1732
| Recommended Budget | [5 empty] | 23376

## SF 78 Electric Z4
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
4
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 95 | 760
|  |  | Disposal | 1 | LS | 500 | 500
1260
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 8000 | 8000
|  |  | Non-ducted mini-split heat pump, 3 indoor units, 4-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 95 | 1520
Controls
|  |  | Thermostat & wiring | 3 | EA | 200 | 600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 5 | EA | 95 | 475
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 95 | 1140
|  | Ductwork modifications |  |  |  |  | None
Miscellaneous supplies
Labor
13435
|  | Subtotal |  |  |  |  | 14695
0
| General Conditions and Overhead |  |  | 18% |  |  | 2645 | 0
| Design and Engineering |  |  | 10% |  |  | 1734
| Permit, testing and inspection |  |  | 1.25% |  |  | 238
| Contractor Profit/Market Factor |  |  | 5% |  |  | 966
| Recommended Budget | [5 empty] | 20278

## SF 78 Electric Z6
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
6
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 7600 | 7600
|  |  | Non-ducted mini-split heat pump, 3 indoor units, 3-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 3 | EA | 200 | 600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 5 | EA | 95 | 475
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 85 | 1020
|  | Ductwork modifications |  |  |  |  | None
Miscellaneous supplies
Labor
12755
|  | Subtotal |  |  |  |  | 13935
0
| General Conditions and Overhead |  |  | 15% |  |  | 2090 | 0
| Design and Engineering |  |  | 10% |  |  | 1603
| Permit, testing and inspection |  |  | 1.25% |  |  | 220
| Contractor Profit/Market Factor |  |  | 2% |  |  | 357
| Recommended Budget | [5 empty] | 18205

## SF 78 Electric Z9
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
9
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 85 | 680
|  |  | Disposal | 1 | LS | 500 | 500
1180
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 8000 | 8000
|  |  | Non-ducted mini-split heat pump, 3 indoor units, 4-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 5 | EA | 100 | 500
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 85 | 1360
Controls
|  |  | Thermostat & wiring | 3 | EA | 200 | 600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 85 | 1020
|  | Ductwork modifications |  |  |  |  | None
Miscellaneous supplies
Labor
13270
|  | Subtotal |  |  |  |  | 14450
0
| General Conditions and Overhead |  |  | 15% |  |  | 2168 | 0
| Design and Engineering |  |  | 10% |  |  | 1662
| Permit, testing and inspection |  |  | 1.25% |  |  | 229
| Contractor Profit/Market Factor |  |  | 2% |  |  | 370
| Recommended Budget | [5 empty] | 18879

## SF 78 Electric Z10
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
10
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 70 | 560
|  |  | Disposal | 1 | LS | 500 | 500
1060
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 6100 | 6100
|  |  | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 70 | 1120
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 70 | 840
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 70 | 560
11160
|  | Subtotal |  |  |  |  | 12220
0
| General Conditions and Overhead |  |  | 15% |  |  | 1833 | 0
| Design and Engineering |  |  | 10% |  |  | 1405
| Permit, testing and inspection |  |  | 1.25% |  |  | 193
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 15651

## SF 78 Electric Z12
Single Family | [8 empty] | Single Family: Pre-1978
Pre-1978
Electric Option
12
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 65 | 520
|  |  | Disposal | 1 | LS | 500 | 500
1020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 6100 | 6100
|  |  | Ducted split heat pump AHU in attic, 5-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 16 | HR | 65 | 1040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 2 | EA | 95 | 190
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 12 | HR | 65 | 780
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 8 | HR | 65 | 520
10980
|  | Subtotal |  |  |  |  | 12000
0
| General Conditions and Overhead |  |  | 15% |  |  | 1800 | 0
| Design and Engineering |  |  | 10% |  |  | 1380
| Permit, testing and inspection |  |  | 1.25% |  |  | 190
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 15370

## LRMF NC Gas Z3 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Gas Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted In-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | No AC |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
12340
|  | Subtotal |  |  |  |  | 14360
0
| General Conditions and Overhead |  |  | 20% |  |  | 2872 | 0
| Design and Engineering |  |  | 10% |  |  | 1723
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 237
| Recommended Budget | [5 empty] | 19192
cell 37 check

## LRMF NC Electric Z3 S (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF NC Electric Z3 O1 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF NC Electric Z3 O2 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF NC Gas Z4 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Gas Option
4
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
12340
|  | Subtotal |  |  |  |  | 14360
0
| General Conditions and Overhead |  |  | 18% |  |  | 2585 | 0
| Design and Engineering |  |  | 10% |  |  | 1695
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 233
| Recommended Budget | [5 empty] | 18873
cell 37 check

## LRMF NC Electric Z4 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
4
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 18% |  |  | 2104 | 0
| Design and Engineering |  |  | 10% |  |  | 1379
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 190
| Recommended Budget | [5 empty] | 15363
cell 37 check

## LRMF NC Gas Z6 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Gas Option
6
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted in-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 1.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
11620
|  | Subtotal |  |  |  |  | 13480
0
| General Conditions and Overhead |  |  | 15% |  |  | 2022 | 0
| Design and Engineering |  |  | 10% |  |  | 1550
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 213
| Recommended Budget | [5 empty] | 17265
cell 37 check

## LRMF NC Electric Z6 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
6
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 85 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 1.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
9110
|  | Subtotal |  |  |  |  | 10970
0
| General Conditions and Overhead |  |  | 15% |  |  | 1646 | 0
| Design and Engineering |  |  | 10% |  |  | 1262
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 173
| Recommended Budget | [5 empty] | 14051
cell 37 check

## LRMF NC Gas Z9 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Gas Option
9
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted in-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
11620
|  | Subtotal |  |  |  |  | 13480
0
| General Conditions and Overhead |  |  | 15% |  |  | 2022 | 0
| Design and Engineering |  |  | 10% |  |  | 1550
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 213
| Recommended Budget | [5 empty] | 17265
cell 37 check

## LRMF NC Electric Z9 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
9
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 85 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
9110
|  | Subtotal |  |  |  |  | 10970
0
| General Conditions and Overhead |  |  | 15% |  |  | 1646 | 0
| Design and Engineering |  |  | 10% |  |  | 1262
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 173
| Recommended Budget | [5 empty] | 14051
cell 37 check

## LRMF NC Gas Z10 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Gas Option
10
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 70 | 1120
|  |  | Disposal | 1 | LS | 500 | 500
1620
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted in-unit furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 70 | 1120
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 70 | 2240
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 70 | 1680
10540
|  | Subtotal |  |  |  |  | 12160
0
| General Conditions and Overhead |  |  | 15% |  |  | 1824 | 0
| Design and Engineering |  |  | 10% |  |  | 1398
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 192
| Recommended Budget | [5 empty] | 15574
cell 37 check

## LRMF NC Electric Z10 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
10
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 70 | 1120
|  |  | Disposal | 1 | LS | 500 | 500
1620
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 70 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton. 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 70 | 2240
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 70 | 1680
8270
|  | Subtotal |  |  |  |  | 9890
0
| General Conditions and Overhead |  |  | 15% |  |  | 1484 | 0
| Design and Engineering |  |  | 10% |  |  | 1137
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 156
| Recommended Budget | [5 empty] | 12667
cell 37 check

## LRMF NC Gas Z12 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Gas Option
12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 65 | 1040
|  |  | Disposal | 1 | LS | 500 | 500
1540
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted in-unit furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 65 | 1040
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 65 | 2080
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 65 | 1560
10180
|  | Subtotal |  |  |  |  | 11720
0
| General Conditions and Overhead |  |  | 15% |  |  | 1758 | 0
| Design and Engineering |  |  | 10% |  |  | 1348
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 185
| Recommended Budget | [5 empty] | 15011
cell 37 check

## LRMF NC Electric Z12 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: New Construction
New Construction
Electric Option
12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 65 | 1040
|  |  | Disposal | 1 | LS | 500 | 500
1540
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 65 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 65 | 2080
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 65 | 1560
7990
|  | Subtotal |  |  |  |  | 9530
0
| General Conditions and Overhead |  |  | 15% |  |  | 1430 | 0
| Design and Engineering |  |  | 10% |  |  | 1096
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 151
| Recommended Budget | [5 empty] | 12207
cell 37 check

## LRMF 90 Gas Z3 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Gas Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Hydronic AHU in-unit, see DHW for water heater info |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 1.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
12340
|  | Subtotal |  |  |  |  | 14360
0
| General Conditions and Overhead |  |  | 20% |  |  | 2872 | 0
| Design and Engineering |  |  | 10% |  |  | 1723
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 237
| Recommended Budget | [5 empty] | 19192
cell 37 check

## LRMF 90 Electric Z3 S (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF 90 Electric Z3 O1 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF 90 Electric Z3 O2 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF 90 Gas Z4 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Gas Option
4
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Hydronic AHU in-unit, see DHW for water heater info |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
12340
|  | Subtotal |  |  |  |  | 14360
0
| General Conditions and Overhead |  |  | 18% |  |  | 2585 | 0
| Design and Engineering |  |  | 10% |  |  | 1695
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 233
| Recommended Budget | [5 empty] | 18873
cell 37 check

## LRMF 90 Electric Z4 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
4
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted split heat pump AHU in-unit, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 18% |  |  | 2104 | 0
| Design and Engineering |  |  | 10% |  |  | 1379
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 190
| Recommended Budget | [5 empty] | 15363
cell 37 check

## LRMF 90 Gas Z6 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Gas Option
6
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Hydronic AHU in-unit, see DHW for water heater info |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
11620
|  | Subtotal |  |  |  |  | 13480
0
| General Conditions and Overhead |  |  | 15% |  |  | 2022 | 0
| Design and Engineering |  |  | 10% |  |  | 1550
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 213
| Recommended Budget | [5 empty] | 17265
cell 37 check

## LRMF 90 Electric Z6 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
6
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 85 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted split heat pump AHU in-unit, 2-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
9110
|  | Subtotal |  |  |  |  | 10970
0
| General Conditions and Overhead |  |  | 15% |  |  | 1646 | 0
| Design and Engineering |  |  | 10% |  |  | 1262
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 173
| Recommended Budget | [5 empty] | 14051
cell 37 check

## LRMF 90 Gas Z9 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Gas Option
9
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Hydronic AHU in-unit, see DHW for water heater info |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
11620
|  | Subtotal |  |  |  |  | 13480
0
| General Conditions and Overhead |  |  | 15% |  |  | 2022 | 0
| Design and Engineering |  |  | 10% |  |  | 1550
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 213
| Recommended Budget | [5 empty] | 17265
cell 37 check

## LRMF 90 Electric Z9 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
9
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 85 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted split heat pump AHU in-unit, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
9110
|  | Subtotal |  |  |  |  | 10970
0
| General Conditions and Overhead |  |  | 15% |  |  | 1646 | 0
| Design and Engineering |  |  | 10% |  |  | 1262
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 173
| Recommended Budget | [5 empty] | 14051
cell 37 check

## LRMF 90 Gas Z10 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Gas Option
10
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 70 | 1120
|  |  | Disposal | 1 | LS | 500 | 500
1620
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Hydronic AHU in-unit, see DHW for water heater info |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 70 | 1120
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 70 | 2240
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 70 | 1680
10540
|  | Subtotal |  |  |  |  | 12160
0
| General Conditions and Overhead |  |  | 15% |  |  | 1824 | 0
| Design and Engineering |  |  | 10% |  |  | 1398
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 192
| Recommended Budget | [5 empty] | 15574
cell 37 check

## LRMF 90 Electric Z10 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
10
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 70 | 1120
|  |  | Disposal | 1 | LS | 500 | 500
1620
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 70 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted split heat pump AHU in-unit, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 70 | 2240
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 70 | 1680
8270
|  | Subtotal |  |  |  |  | 9890
0
| General Conditions and Overhead |  |  | 15% |  |  | 1484 | 0
| Design and Engineering |  |  | 10% |  |  | 1137
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 156
| Recommended Budget | [5 empty] | 12667
cell 37 check

## LRMF 90 Gas Z12 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Gas Option
12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 65 | 1040
|  |  | Disposal | 1 | LS | 500 | 500
1540
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Hydronic AHU in-unit, see DHW for water heater info |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 65 | 1040
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 65 | 2080
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 65 | 1560
10180
|  | Subtotal |  |  |  |  | 11720
0
| General Conditions and Overhead |  |  | 15% |  |  | 1758 | 0
| Design and Engineering |  |  | 10% |  |  | 1348
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 185
| Recommended Budget | [5 empty] | 15011
cell 37 check

## LRMF 90 Electric Z12 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: 1990's
1990's
Electric Option
12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 65 | 1040
|  |  | Disposal | 1 | LS | 500 | 500
1540
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 65 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Ducted split heat pump AHU in-unit, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 65 | 2080
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 65 | 1560
7990
|  | Subtotal |  |  |  |  | 9530
0
| General Conditions and Overhead |  |  | 15% |  |  | 1430 | 0
| Design and Engineering |  |  | 10% |  |  | 1096
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 151
| Recommended Budget | [5 empty] | 12207
cell 37 check

## LRMF 78 Gas Z3 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Window AC, 2 units, 11-11.2 CEER, 1.5-ton |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
12340
|  | Subtotal |  |  |  |  | 14360
0
| General Conditions and Overhead |  |  | 20% |  |  | 2872 | 0
| Design and Engineering |  |  | 10% |  |  | 1723
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 237
| Recommended Budget | [5 empty] | 19192
cell 37 check

## LRMF 78 Electric Z3 S (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 2-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF 78 Electric Z3 O1 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 2-ton 7.6 EER, 2.5 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 20% |  |  | 2338 | 0
| Design and Engineering |  |  | 10% |  |  | 1403
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 193
| Recommended Budget | [5 empty] | 15624
cell 37 check

## LRMF 78 Gas Z4 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
4
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 95 | 1520
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Window AC, 2 units, 11-11.2 CEER, 3-ton |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
12340
|  | Subtotal |  |  |  |  | 14360
0
| General Conditions and Overhead |  |  | 18% |  |  | 2585 | 0
| Design and Engineering |  |  | 10% |  |  | 1695
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 233
| Recommended Budget | [5 empty] | 18873
cell 37 check

## LRMF 78 Electric Z4 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
4
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 95 | 1520
|  |  | Disposal | 1 | LS | 500 | 500
2020
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 95 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 3-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 95 | 3040
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 95 | 2280
9670
|  | Subtotal |  |  |  |  | 11690
0
| General Conditions and Overhead |  |  | 18% |  |  | 2104 | 0
| Design and Engineering |  |  | 10% |  |  | 1379
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 190
| Recommended Budget | [5 empty] | 15363
cell 37 check

## LRMF 78 Gas Z6 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
6
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Window AC, 2 units, 11-11.2 CEER, 2-ton |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
11620
|  | Subtotal |  |  |  |  | 13480
0
| General Conditions and Overhead |  |  | 15% |  |  | 2022 | 0
| Design and Engineering |  |  | 10% |  |  | 1550
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 213
| Recommended Budget | [5 empty] | 17265
cell 37 check

## LRMF 78 Electric Z6 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
6
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 85 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 2-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
9110
|  | Subtotal |  |  |  |  | 10970
0
| General Conditions and Overhead |  |  | 15% |  |  | 1646 | 0
| Design and Engineering |  |  | 10% |  |  | 1262
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 173
| Recommended Budget | [5 empty] | 14051
cell 37 check

## LRMF 78 Gas Z9 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
9
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 85 | 1360
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Window AC, 2 units, 11-11.2 CEER, 3-ton |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
11620
|  | Subtotal |  |  |  |  | 13480
0
| General Conditions and Overhead |  |  | 15% |  |  | 2022 | 0
| Design and Engineering |  |  | 10% |  |  | 1550
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 213
| Recommended Budget | [5 empty] | 17265
cell 37 check

## LRMF 78 Electric Z9 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
9
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 85 | 1360
|  |  | Disposal | 1 | LS | 500 | 500
1860
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 85 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 3-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 85 | 2720
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 85 | 2040
9110
|  | Subtotal |  |  |  |  | 10970
0
| General Conditions and Overhead |  |  | 15% |  |  | 1646 | 0
| Design and Engineering |  |  | 10% |  |  | 1262
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 173
| Recommended Budget | [5 empty] | 14051
cell 37 check

## LRMF 78 Gas Z10 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
10
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 70 | 1120
|  |  | Disposal | 1 | LS | 500 | 500
1620
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Gravity wall furnace, 64-65 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 70 | 1120
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Window AC, 2 units, 11-11.2 CEER, 4-ton |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 70 | 2240
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 70 | 1680
10540
|  | Subtotal |  |  |  |  | 12160
0
| General Conditions and Overhead |  |  | 15% |  |  | 1824 | 0
| Design and Engineering |  |  | 10% |  |  | 1398
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 192
| Recommended Budget | [5 empty] | 15574
cell 37 check

## LRMF 78 Electric Z10 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
10
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 70 | 1120
|  |  | Disposal | 1 | LS | 500 | 500
1620
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 70 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 4-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 70 | 2240
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 70 | 1680
8270
|  | Subtotal |  |  |  |  | 9890
0
| General Conditions and Overhead |  |  | 15% |  |  | 1484 | 0
| Design and Engineering |  |  | 10% |  |  | 1137
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 156
| Recommended Budget | [5 empty] | 12667
cell 37 check

## LRMF 78 Gas Z12 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 65 | 1040
|  |  | Disposal | 1 | LS | 500 | 500
1540
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Gravity wall furnace, 64-65 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | 65 | 1040
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Window AC, 2 units, 11-11.2 CEER, 4-ton |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 65 | 2080
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 65 | 1560
10180
|  | Subtotal |  |  |  |  | 11720
0
| General Conditions and Overhead |  |  | 15% |  |  | 1758 | 0
| Design and Engineering |  |  | 10% |  |  | 1348
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 185
| Recommended Budget | [5 empty] | 15011
cell 37 check

## LRMF 78 Electric Z12 (hidden)
Low-Rise Multi-Family | [8 empty] | Low-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | 65 | 1040
|  |  | Disposal | 1 | LS | 500 | 500
1540
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price |  | EA |  | 0
|  |  | Heating included in split system heat pump |  |  |  | 0
|  |  | Miscellaneous supplies |  | LS |  | 0
|  |  | Labor |  | HR | 65 | 0
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Packaged terminal heat pump, 4-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | 65 | 2080
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | 65 | 1560
7990
|  | Subtotal |  |  |  |  | 9530
0
| General Conditions and Overhead |  |  | 15% |  |  | 1430 | 0
| Design and Engineering |  |  | 10% |  |  | 1096
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 151
| Recommended Budget | [5 empty] | 12207
cell 37 check

## HRMF NC Gas Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HVAC (hidden)
HVAC
|  |  | Zone | Existing |  | Gas Technology |  | Electric tech
Single Family
|  | New Construction | 3 | - | - | Ducted Furnace | no AC | Ducted Split Heat Pump
|  |  | 6, 4, 9, 10, 12 | - | - | Ducted Furnace | Split AC | Ducted Split Heat Pump
|  | 1990's | 3, 6 | Ducted Furnace | No AC | New Furnace | AC | Ducted Split Heat Pump
|  |  | 4, 9, 10, 12 | Ducted Furnace | Split AC | New Furnace | AC | Ducted Split Heat Pump
|  | Pre 1978 | 3, 6 | Wall Furnace | No AC | New Ducted Furnace, addition of ducts | AC | Non-ducted MSHP, Multi-head
|  |  | 4, 9 | Wall Furnace | Window AC | New Furnace, addition of ducts |  | Non-ducted MSHP, Multi-head
|  |  | 10, 12 | Ducted Furnace | Split AC | New Furnace | AC | Ducted Split Heat Pump
Low-Rise Multi-Family
|  | New Construction | 3 | - | - | Ducted Furnace | no AC | New Ducted mini-split heat pump
|  |  | 6, 4, 9, 10, 12 | - | - | Ducted Furnace | Split AC | New Ducted mini-split heat pump
|  | 1990's | 3, 6 | Combined Hydronic | No AC | Combined hydronic | Split AC | Ducted Split Heat Pump
|  |  | 4, 9, 10, 12 | Combined Hydronic | Split AC | Combined hydronic | Split AC | Ducted Split Heat Pump
|  | Pre 1978 | 3, 6 | Wall Furnace | No AC | New Wall Furnace | Window AC | Packaged Thermal Heat Pump
|  |  | 4, 9 | Wall Furnace | Window AC | New Wall Furnace | Window AC | Packaged Thermal Heat Pump
High-Rise Multi-Family
|  | New Construction | 3 | - | - | Hydronic Heating only FCU, Central Condensing Gas Boiler | No AC | Electric Resistance + ERV | No AC
|  |  | 6, 4, 9, 10, 12 | - | - | In-unit 4-pipe fan coil units connected to central natural gas boiler and chiller/cooling towers |  | VRF
|  | 1990's | 3 | Hydronic Heating only FCU, Central Gas Boiler | No AC | Update with new combined gas boiler | No AC
|  |  | 6, 4, 9, 10, 12 | In-unit 4-pipe fan coil units connected to central condensing gas boiler and existing chiller/cooling towers |  | Keep existing system with updated condensing gas boiler and existing chiller/coolant towers |  | Keep existing system, replace boiler with ASHP water heater, keep existing chiller/cooling tower
|  | Pre 1978 | 3 | Hydronic radiators, central gas boiler | No AC | Update with new condensing gas boiler | No AC | Keep existing system, replace boiler with new central AHP | No AC
|  |  | 6, 4, 9, 10, 12 | Hydronic radiators, central gas boiler | Window AC | Keep hydronic radiators, update central gas boiler with condensig gas boiler | Window AC | Abandon prior heating system and replace AC unit with PTHP for heating and cooling