## Summary
|  | O1 | A3 | A4 | h48 |  | D15 | D20 | H10 | H35 | H39 | H41 | H43 | H45
Heating and Air Conditioning | Description | Building Type | Fuel Option | Climate Zone | Recommended Budget | Per Unit Budget | Space Heating Technologies | Space Cooling Technologies | Demolition | Installation | General Conditions and Overhead | Design and Engineering | Permit, testing and inspection | Contractor Profit/Market Factor
| LRMF NC Gas Z3 | Low Rise Multi-Family: New Construction | Gas Option | 3 | 31475.3159 | 3934.4145 | Ducted In-unit furnace 80 AFUE, 40 kBtu/h | No AC | 0 | 27422.3159 | 2468 | 1196 | 389 | 0
| LRMF NC Gas Z6 | Low Rise Multi-Family: New Construction | Gas Option | 6 | 71705.4739 | 8963.1842 | Ducted in-unit furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 1.5 tons | 0 | 62473.4739 | 5623 | 2724 | 885 | 0
| LRMF NC Gas Z4 | Low Rise Multi-Family: New Construction | Gas Option | 4 | 79051.4739 | 9881.4342 | Ducted In-unit furnace 80 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2 tons | 0 | 68873.4739 | 6199 | 3003 | 976 | 0
| LRMF NC Gas Z10 | Low Rise Multi-Family: New Construction | Gas Option | 10 | 83642.4739 | 10455.3092 | Ducted in-unit furnace 80 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 2.5 tons | 0 | 72873.4739 | 6559 | 3177 | 1033 | 0
| LRMF NC Electric Z6 | Low Rise Multi-Family: New Construction | Electric Option | 6 | 63261.737 | 7907.7171 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 1.5-ton 21 SEER/13 EER, 11 HSPF | 0 | 55116.737 | 4961 | 2403 | 781 | 0
| LRMF NC Electric Z6 O2 | Low Rise Multi-Family: New Construction | Electric Option | 6 | 77571.4036 | 9696.4255 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 1.5-ton 30 SEER/15 EER, 14 HSPF | 0 | 67583.4036 | 6083 | 2947 | 958 | 0
| LRMF NC Electric Z10 | Low Rise Multi-Family: New Construction | Electric Option | 10 | 70607.737 | 8825.9671 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton 21 SEER/13 EER, 11 HSPF | 0 | 61516.737 | 5537 | 2682 | 872 | 0
| LRMF NC Electric Z12 O2 | Low Rise Multi-Family: New Construction | Electric Option | 12 | 87518.0703 | 10939.7588 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton 30 SEER/15 EER, 14 HSPF | 0 | 76250.0703 | 6863 | 3325 | 1080 | 0
| LRMF NC Electric Z3 O1 | Low Rise Multi-Family: New Construction | Electric Option | 3 | 64179.737 | 8022.4671 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF | 0 | 55916.737 | 5033 | 2438 | 792 | 0
| LRMF NC Electric Z3 S | Low Rise Multi-Family: New Construction | Electric Option | 3 | 66934.737 | 8366.8421 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF | 0 | 58316.737 | 5249 | 2543 | 826 | 0
| LRMF NC Electric Z3 O2 | Low Rise Multi-Family: New Construction | Electric Option | 3 | 82544.737 | 10318.0921 | Heating included in split system heat pump | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF | 0 | 71916.737 | 6473 | 3136 | 1019 | 0
| LRMF NC Gas Cond Z3 | Low Rise Multi-Family: New Construction | Gas Furnace - Condensing | 3 | 34443.9896 | 4305.4987 | Ducted In-unit furnace 90 AFUE, 40 kBtu/h | No AC | 0 | 30009.9896 | 2701 | 1308 | 425 | 0
| LRMF NC Gas Cond Z6 | Low Rise Multi-Family: New Construction | Gas Furnace - Condensing + A/C | 6 | 74676.1476 | 9334.5184 | Ducted in-unit furnace 90 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 1.5 tons | 0 | 65061.1476 | 5856 | 2837 | 922 | 0
| LRMF NC Gas Cond Z4 | Low Rise Multi-Family: New Construction | Gas Furnace - Condensing + A/C | 4 | 82022.1476 | 10252.7684 | Ducted In-unit furnace 90 AFUE, 40 kBtu/h | Split AC 14 SEER/12.2 EER, 2 tons | 0 | 71461.1476 | 6432 | 3116 | 1013 | 0
| LRMF NC Gas Cond Z9 | Low Rise Multi-Family: New Construction | Gas Furnace - Condensing + A/C | 9 | 86888.1476 | 10861.0184 | Ducted in-unit furnace 90 AFUE, 60 kBtu/h | Split AC 14 SEER/12.2 EER, 2.5 tons | 0 | 75701.1476 | 6813 | 3301 | 1073 | 0
| LRMF NC Elec Baseboard Z3 | Low Rise Multi-Family: New Construction | Electric Resistance Baseboard | 3 | 15113.4386 | 1889.1798 | 32 Electric baseboard heaters, 4 kW each | No AC | 0 | 13167.4386 | 1185 | 574 | 187 | 0
| LRMF NC Elec Baseboard Z6 | Low Rise Multi-Family: New Construction | Electric Resistance Baseboard + A/C | 6 | 58328.5966 | 7291.0746 | 32 Electric baseboard heaters, 4 kW each | Split AC 14 SEER/12.2 EER, 1.5 tons | 0 | 50818.5966 | 4574 | 2216 | 720 | 0
| LRMF NC Elec Baseboard Z4 | Low Rise Multi-Family: New Construction | Electric Resistance Baseboard + A/C | 4 | 65674.5966 | 8209.3246 | 32 Electric baseboard heaters, 4 kW each | Split AC 14 SEER/12.2 EER, 2 tons | 0 | 57218.5966 | 5150 | 2495 | 811 | 0
| LRMF NC Elec Baseboard Z10 | Low Rise Multi-Family: New Construction | Electric Resistance Baseboard + A/C | 10 | 70163.6602 | 8770.4575 | 36 Electric baseboard heaters, 4 kW each | Split AC 14 SEER/12.2 EER, 2.5 tons | 0 | 61130.6602 | 5502 | 2665 | 866 | 0
| LRMF NC Electric Z6 DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 6 | 53160.737 | 6645.0921 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 1.5-ton 21 SEER/13 EER, 11 HSPF | 0 | 46316.737 | 4169 | 2019 | 656 | 0
| LRMF NC Electric Z6 O2 DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 6 | 63892.737 | 7986.5921 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 1.5-ton 30 SEER/15 EER, 14 HSPF | 0 | 55666.737 | 5010 | 2427 | 789 | 0
| LRMF NC Electric Z10 DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 10 | 58670.737 | 7333.8421 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 2.5-ton 21 SEER/13 EER, 11 HSPF | 0 | 51116.737 | 4601 | 2229 | 724 | 0
| LRMF NC Electric Z12 O2 DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 12 | 71352.737 | 8919.0921 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 2.5-ton 30 SEER/15 EER, 14 HSPF | 0 | 62166.737 | 5595 | 2710 | 881 | 0
| LRMF NC Electric Z3 O1 DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 3 | 53850.737 | 6731.3421 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF | 0 | 46916.737 | 4223 | 2046 | 665 | 0
| LRMF NC Electric Z3 S DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 3 | 55915.737 | 6989.4671 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 2-ton 21 SEER/13 EER, 11 HSPF | 0 | 48716.737 | 4385 | 2124 | 690 | 0
| LRMF NC Electric Z3 O2 DL | Low Rise Multi-Family: New Construction | Ductless Heat Pump | 3 | 67623.737 | 8452.9671 | Heating included in split system heat pump | Ductless mini-split heat pump, wall-mounted interior unit, 2-ton 30 SEER/15 EER, 14 HSPF | 0 | 58916.737 | 5303 | 2569 | 835 | 0
Please note that climate zone identifiers (e.g. Z3, Z4, Z6, Z9, and Z12) are inherited from the original datasets representing California's climate zones. They are neglected and have no impacts on this Utah-specific cost estimate practice
Please note that the AECOM ID in the summary spreadsheet can be used to locate detailed cost data in AECOM datasets ("Description" column in the Summary table or tab names)

## Cost Assumptions
Zone |  | Labor | OH&P | Design | Test & Inspect | Market
3 | Sacramento | 58.8662 | 15% | 10% | 1.25% | 0%
4 | Sacramento | 58.8662 | 15% | 10% | 1.25% | 0%
6 | Sacramento | 58.8662 | 15% | 10% | 1.25% | 0%
9 | Sacramento | 58.8662 | 15% | 10% | 1.25% | 0%
10 | Sacramento | 58.8662 | 15% | 10% | 1.25% | 0%
12 | Sacramento | 58.8662 | 15% | 10% | 1.25% | 0%

## LRMF NC Elec Baseboard
Single Family
New Construction |  |  |  |  | LRMF NC Elec Baseboard Z3 |  |  | LRMF NC Elec Baseboard Z6 |  |  | LRMF NC Elec Baseboard Z4 |  |  | LRMF NC Elec Baseboard Z10
Electric Option |  |  |  |  | 32 Electric baseboard heaters, 4 kW each |  |  | 32 Electric baseboard heaters, 4 kW each |  |  | 32 Electric baseboard heaters, 4 kW each |  |  | 36 Electric baseboard heaters, 4 kW each
[5 empty] | No AC |  |  | Split AC 14 SEER/12.2 EER, 1.5 tons |  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  | Split AC 14 SEER/12.2 EER, 2.5 tons
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | HR
|  |  | Disposal | LS
| Installation | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0
Furnace
|  |  | New Furnace, equipment price | EA | 32 | 150 | 4800 | 32 | 150 | 4800 | 32 | 150 | 4800 | 36 | 150 | 5400
Ducted attic furnace
|  |  | Miscellaneous supplies | LS | 32 | 50 | 1600 | 32 | 50 | 1600 | 32 | 50 | 1600 | 36 | 50 | 1800
|  |  | Labor | HR | 24 | 58.8662 | 1412.7895 | 24 | 58.8662 | 1412.7895 | 24 | 58.8662 | 1412.7895 | 27 | 58.8662 | 1589.3882
Air Conditioner
|  |  | New Air Conditioner, equipment price |  |  |  |  | 8 | 2700 | 21600 | 8 | 3500 | 28000 | 8 | 3800 | 30400
Split AC 14 SEER/12.2 EER, 2.5 tons
|  |  | Concrete pad, precast |  |  |  |  | 8 | 100 | 800 | 8 | 100 | 800 | 8 | 100 | 800
|  |  | Refrigerant piping and refrigerant |  |  |  |  | 800 | 4 | 3200 | 800 | 4 | 3200 | 800 | 4 | 3200
|  |  | Miscellaneous supplies |  |  |  |  | 8 | 400 | 3200 | 8 | 400 | 3200 | 8 | 400 | 3200
|  |  | Labor |  |  |  |  | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | EA |  |  | Included with baseboard heater | 8 | 400 | 3200 | 8 | 400 | 3200 | 8 | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | EA | 40 | 75 | 3000 | 40 | 75 | 3000 | 40 | 75 | 3000 | 44 | 75 | 3300
|  |  | Panel and main service modification |  |  |  | Not required |  |  | Not required |  |  | Not required |  |  | Not required
|  |  | Gas supply piping | LF |  |  | Not required |  |  | Not required |  |  | Not required |  |  | Not required
|  |  | Labor | HR | 40 | 58.8662 | 2354.6492 | 40 | 58.8662 | 2354.6492 | 40 | 58.8662 | 2354.6492 | 44 | 58.8662 | 2590.1141
Ductwork connections (excludes distributed ductwork)
|  |  | Ductwork | [6 empty] | Included in installation |  |  | Included in installation |  |  | Included in installation
|  |  | Labor | [6 empty] | Included in installation |  |  | Included in installation |  |  | Included in installation
[7 empty] | 13167.4386 |  |  | 50818.5966 |  |  | 57218.5966 |  |  | 61130.6602
|  | Subtotal |  |  |  |  | 13167.4386 |  |  | 50818.5966 |  |  | 57218.5966 |  |  | 61130.6602
| General Conditions and Overhead |  |  |  | 9% |  | 1185 | 9% |  | 4574 | 9% |  | 5150 | 9% |  | 5502
| Design and Engineering |  |  |  | 4% |  | 574 | 4% |  | 2216 | 4% |  | 2495 | 4% |  | 2665
| Permit, testing and inspection |  |  |  | 1.25% |  | 187 | 1.25% |  | 720 | 1.25% |  | 811 | 1.25% |  | 866
Contractor Profit/Market Factor
| Recommended Budget | [5 empty] | 15113.4386 |  |  | 58328.5966 |  |  | 65674.5966 |  |  | 70163.6602
[7 empty] | 4909.3246 |  |  | 11500.1842 |  |  | 11844.1842 |  |  | 12294.9167

## LRMF NC Gas Condensing
Single Family
New Construction |  |  |  |  | LRMF NC Gas Cond Z3 |  |  | LRMF NC Gas Cond Z6 |  |  | LRMF NC Gas Cond Z4 |  |  | LRMF NC Gas Cond Z9
Gas Option |  |  |  |  | Ducted attic furnace 90 AFUE, 40 kBtu/h |  |  | Ducted attic furnace 90 AFUE, 40 kBtu/h |  |  | Ducted attic furnace 90 AFUE, 40 kBtu/h |  |  | Ducted attic furnace 90 AFUE, 60 kBtu/h
[5 empty] | No AC |  |  | Split AC 14 SEER/12.2 EER, 1.5 tons |  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  | Split AC 14 SEER/12.2 EER, 2.5 tons
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | HR
|  |  | Disposal | LS
| Installation | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0
Furnace
|  |  | New Furnace, equipment price | EA | 8 | 1380 | 11040 | 8 | 1380 | 11040 | 8 | 1380 | 11040 | 8 | 1610 | 12880
Ducted attic furnace
|  |  | Miscellaneous supplies | LS | 8 | 287.5 | 2300 | 8 | 287.5 | 2300 | 8 | 287.5 | 2300 | 8 | 287.5 | 2300
|  |  | Labor | HR | 110.4 | 58.8662 | 6498.8317 | 110.4 | 58.8662 | 6498.8317 | 110.4 | 58.8662 | 6498.8317 | 110.4 | 58.8662 | 6498.8317
Air Conditioner
|  |  | New Air Conditioner, equipment price |  |  |  |  | 8 | 2700 | 21600 | 8 | 3500 | 28000 | 8 | 3800 | 30400
Split AC 14 SEER/12.2 EER, 2.5 tons
|  |  | Concrete pad, precast |  |  |  |  | 8 | 100 | 800 | 8 | 100 | 800 | 8 | 100 | 800
|  |  | Refrigerant piping and refrigerant |  |  |  |  | 800 | 4 | 3200 | 800 | 4 | 3200 | 800 | 4 | 3200
|  |  | Miscellaneous supplies |  |  |  |  | 8 | 400 | 3200 | 8 | 400 | 3200 | 8 | 400 | 3200
|  |  | Labor |  |  |  |  | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | EA | 8 | 400 | 3200 | 8 | 400 | 3200 | 8 | 400 | 3200 | 8 | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | EA | 8 | 75 | 600 | 16 | 75 | 1200 | 16 | 75 | 1200 | 16 | 75 | 1200
|  |  | Panel and main service modification |  |  |  | Not required |  |  | Not required |  |  | Not required |  |  | Not required
|  |  | Gas supply piping | LF | 240 | 3 | 720 | 240 | 3 | 720 | 240 | 3 | 720 | 240 | 3 | 720
|  |  | Labor | HR | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158 | 96 | 58.8662 | 5651.158
Ductwork connections (excludes distributed ductwork)
|  |  | Ductwork |  |  |  | Included in installation |  |  | Included in installation |  |  | Included in installation |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation |  |  | Included in installation |  |  | Included in installation |  |  | Included in installation
[7 empty] | 30009.9896 |  |  | 65061.1476 |  |  | 71461.1476 |  |  | 75701.1476
|  | Subtotal |  |  |  |  | 30009.9896 |  |  | 65061.1476 |  |  | 71461.1476 |  |  | 75701.1476
| General Conditions and Overhead |  |  |  | 9% |  | 2701 | 9% |  | 5856 | 9% |  | 6432 | 9% |  | 6813
| Design and Engineering |  |  |  | 4% |  | 1308 | 4% |  | 2837 | 4% |  | 3116 | 4% |  | 3301
| Permit, testing and inspection |  |  |  | 1.25% |  | 425 | 1.25% |  | 922 | 1.25% |  | 1013 | 1.25% |  | 1073
Contractor Profit/Market Factor
| Recommended Budget | [5 empty] | 34443.9896 |  |  | 74676.1476 |  |  | 82022.1476 |  |  | 86888.1476

## LRMF NC Gas Z3
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Gas Option
3
Demolition
|  | Remove existing furnace |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 1200 | 9600
|  |  | Ducted In-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | None
New Air Conditioner, equipment price
No AC
Concrete pad, precast
Refrigerant piping and refrigerant
Miscellaneous supplies
Labor
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 75 | 600
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping | 240 | LF | 3 | 720
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
27422.3159
|  | Subtotal |  |  |  |  | 27422.3159
0
| General Conditions and Overhead |  |  | 9% |  |  | 2468 | 0
| Design and Engineering |  |  | 4% |  |  | 1196 | 0
| Permit, testing and inspection |  |  | 1.25% |  |  | 389 | 0
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 31475.3159

## LRMF NC Gas Z4
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Gas Option
4
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 1200 | 9600
|  |  | Ducted In-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3500 | 28000
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 75 | 1200
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 240 | LF | 3 | 720
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
68873.4739
|  | Subtotal |  |  |  |  | 68873.4739
0
| General Conditions and Overhead |  |  | 9% |  |  | 6199 | 0
| Design and Engineering |  |  | 4% |  |  | 3003
| Permit, testing and inspection |  |  | 1.25% |  |  | 976
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 79051.4739

## LRMF NC Gas Z6
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Gas Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 1200 | 9600
|  |  | Ducted in-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 2700 | 21600
|  |  | Split AC 14 SEER/12.2 EER, 1.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 75 | 1200
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 240 | LF | 3 | 720
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
62473.4739
|  | Subtotal |  |  |  |  | 62473.4739
0
| General Conditions and Overhead |  |  | 9% |  |  | 5623 | 0
| Design and Engineering |  |  | 4% |  |  | 2724
| Permit, testing and inspection |  |  | 1.25% |  |  | 885
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 71705.4739

## LRMF NC Gas Z9 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Gas Option
9
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 1200 | 9600
|  |  | Ducted in-unit furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3500 | 28000
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 75 | 1200
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 240 | LF | 3 | 720
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
68873.4739
|  | Subtotal |  |  |  |  | 68873.4739
0
| General Conditions and Overhead |  |  | 9% |  |  | 6199 | 0
| Design and Engineering |  |  | 4% |  |  | 3003
| Permit, testing and inspection |  |  | 1.25% |  |  | 976
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 79051.4739

## LRMF NC Gas Z10
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Gas Option
10
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 1400 | 11200
|  |  | Ducted in-unit furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3800 | 30400
|  |  | Split AC 14 SEER/12.2 EER, 2.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 75 | 1200
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 240 | LF | 3 | 720
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
72873.4739
|  | Subtotal |  |  |  |  | 72873.4739
0
| General Conditions and Overhead |  |  | 9% |  |  | 6559 | 0
| Design and Engineering |  |  | 4% |  |  | 3177
| Permit, testing and inspection |  |  | 1.25% |  |  | 1033
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 83642.4739

## LRMF NC Gas Z12 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Gas Option
12
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 1400 | 11200
|  |  | Ducted in-unit furnace 80 AFUE, 60 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3800 | 30400
|  |  | Split AC 14 SEER/12.2 EER, 2.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 75 | 1200
|  |  | Panel and main service modification |  | EA |  | Not required
|  |  | Gas supply piping | 240 | LF | 3 | 720
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
72873.4739
|  | Subtotal |  |  |  |  | 72873.4739
0
| General Conditions and Overhead |  |  | 9% |  |  | 6559 | 0
| Design and Engineering |  |  | 4% |  |  | 3177
| Permit, testing and inspection |  |  | 1.25% |  |  | 1033
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 83642.4739

## LRMF 90 Gas Z3 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Gas Option
3
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 6 | LS | 500 | 3000
4412.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 6 | EA | 1200 | 7200
|  |  | Hydronic AHU in-unit |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 3200 | 19200
|  |  | Split AC 14 SEER/12.2 EER, 1.5 tons |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 6 | EA | 95 | 570
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
50485.1054
|  | Subtotal |  |  |  |  | 54897.8949
0
| General Conditions and Overhead |  |  | 15% |  |  | 8235 | 0
| Design and Engineering |  |  | 10% |  |  | 6313
| Permit, testing and inspection |  |  | 1.25% |  |  | 868
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
0
| Recommended Budget | [5 empty] | 70313.8949
0

## LRMF 90 Gas Z4 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Gas Option
4
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 6 | LS | 500 | 3000
4412.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 6 | EA | 1400 | 8400
|  |  | Hydronic AHU in-unit |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 3600 | 21600
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 6 | EA | 95 | 570
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
54085.1054
|  | Subtotal |  |  |  |  | 58497.8949
0
| General Conditions and Overhead |  |  | 15% |  |  | 8775 | 0
| Design and Engineering |  |  | 10% |  |  | 6727
| Permit, testing and inspection |  |  | 1.25% |  |  | 925
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 74924.8949

## LRMF 90 Gas Z6 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Gas Option
6
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 6 | LS | 500 | 3000
4412.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 6 | EA | 1200 | 7200
|  |  | Hydronic AHU in-unit |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 3400 | 20400
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 6 | EA | 95 | 570
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
51685.1054
|  | Subtotal |  |  |  |  | 56097.8949
0
| General Conditions and Overhead |  |  | 15% |  |  | 8415 | 0
| Design and Engineering |  |  | 10% |  |  | 6451
| Permit, testing and inspection |  |  | 1.25% |  |  | 887
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
0
| Recommended Budget | [5 empty] | 71850.8949
0

## LRMF 90 Gas Z9 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Gas Option
9
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 6 | LS | 500 | 3000
4412.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 6 | EA | 1400 | 8400
|  |  | Hydronic AHU in-unit |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 3600 | 21600
|  |  | Split AC 14 SEER/12.2 EER, 3 tons |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 6 | EA | 95 | 570
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
54085.1054
|  | Subtotal |  |  |  |  | 58497.8949
0
| General Conditions and Overhead |  |  | 15% |  |  | 8775 | 0
| Design and Engineering |  |  | 10% |  |  | 6727
| Permit, testing and inspection |  |  | 1.25% |  |  | 925
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 74924.8949

## LRMF 90 Gas Z10 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Gas Option
10
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 6 | LS | 500 | 3000
4412.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 6 | EA | 1800 | 10800
|  |  | Hydronic AHU in-unit |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 4800 | 28800
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 6 | EA | 95 | 570
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
63685.1054
|  | Subtotal |  |  |  |  | 68097.8949
0
| General Conditions and Overhead |  |  | 15% |  |  | 10215 | 0
| Design and Engineering |  |  | 10% |  |  | 7831
| Permit, testing and inspection |  |  | 1.25% |  |  | 1077
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 87220.8949

## LRMF 90 Gas Z12 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Gas Option
12
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 6 | LS | 500 | 3000
4412.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 6 | EA | 1600 | 9600
|  |  | Hydronic AHU in-unit |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 4800 | 28800
|  |  | Split AC 14 SEER/12.2 EER, 4 tons |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 6 | EA | 95 | 570
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
62485.1054
|  | Subtotal |  |  |  |  | 66897.8949
0
| General Conditions and Overhead |  |  | 15% |  |  | 10035 | 0
| Design and Engineering |  |  | 10% |  |  | 7693
| Permit, testing and inspection |  |  | 1.25% |  |  | 1058
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 85683.8949

## LRMF 78 Gas Z3 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  |  | Disposal | 8 | LS | 500 | 4000
6825.579
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 950 | 7600
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 16 | EA | 800 | 12800
|  |  | Window AC, 2 units, 11-11.2 CEER, 1.5-ton |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 200 | 1600
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 95 | 760
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Not required
|  |  | Wall/Ceiling patch |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
41146.0353
|  | Subtotal |  |  |  |  | 47971.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 7196 | 0
| Design and Engineering |  |  | 10% |  |  | 5517
Permit, testing and inspection
|  |  |  | 0% |  |  | 0
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 759
| Recommended Budget | [5 empty] | 61443.6142

## LRMF 78 Gas Z4 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
4
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  |  | Disposal | 8 | LS | 500 | 4000
6825.579
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 950 | 7600
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 16 | EA | 1200 | 19200
|  |  | Window AC, 2 units, 11-11.2 CEER, 3-ton |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 200 | 1600
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Not required
|  |  | Wall/Ceiling patch |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
47786.0353
|  | Subtotal |  |  |  |  | 54611.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 8192 | 0
| Design and Engineering |  |  | 10% |  |  | 6280
Permit, testing and inspection
|  |  |  | 0% |  |  | 0
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 864
| Recommended Budget | [5 empty] | 69947.6142

## LRMF 78 Gas Z6 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
6
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  |  | Disposal | 8 | LS | 500 | 4000
6825.579
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 950 | 7600
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 16 | EA | 1000 | 16000
|  |  | Window AC, 2 units, 11-11.2 CEER, 2-ton |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 200 | 1600
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 95 | 760
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Not required
|  |  | Wall/Ceiling patch |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
44346.0353
|  | Subtotal |  |  |  |  | 51171.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 7676 | 0
| Design and Engineering |  |  | 10% |  |  | 5885
Permit, testing and inspection
|  |  |  | 0% |  |  | 0
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 809
| Recommended Budget | [5 empty] | 65541.6142

## LRMF 78 Gas Z9 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
9
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  |  | Disposal | 8 | LS | 500 | 4000
6825.579
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 950 | 7600
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 16 | EA | 1200 | 19200
|  |  | Window AC, 2 units, 11-11.2 CEER, 3-ton |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 200 | 1600
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | New ductwork throughout, including patch and repair |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Not required
|  |  | Wall/Ceiling patch |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
47786.0353
|  | Subtotal |  |  |  |  | 54611.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 8192 | 0
| Design and Engineering |  |  | 10% |  |  | 6280
Permit, testing and inspection
|  |  |  | 0% |  |  | 0
| Contractor Profit/Market Factor |  |  | 1.25% |  |  | 864
| Recommended Budget | [5 empty] | 69947.6142

## LRMF 78 Gas Z10 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
10
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  |  | Disposal | 8 | LS | 500 | 4000
6825.579
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 950 | 7600
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 16 | EA | 1400 | 22400
|  |  | Window AC, 2 units, 11-11.2 CEER, 4-ton |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 200 | 1600
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
Not required
|  | Subtotal |  |  |  |  | 57811.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 8672 | 0
| Design and Engineering |  |  | 10% |  |  | 6648
| Permit, testing and inspection |  |  | 1.25% |  |  | 914
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 74045.6142

## LRMF 78 Gas Z12 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
12
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  |  | Disposal | 8 | LS | 500 | 4000
6825.579
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 8 | EA | 950 | 7600
|  |  | Gravity wall furnace, 64-65 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 8 | LS | 250 | 2000
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 16 | EA | 1400 | 22400
|  |  | Window AC, 2 units, 11-11.2 CEER, 4-ton |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 200 | 1600
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  |  |  | Existing
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
Not required
|  | Subtotal |  |  |  |  | 57811.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 8672 | 0
| Design and Engineering |  |  | 10% |  |  | 6648
| Permit, testing and inspection |  |  | 1.25% |  |  | 914
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 74045.6142

## LRMF NC Electric Z3 S
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4800 | 38400
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
58316.737
|  | Subtotal |  |  |  |  | 58316.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5249 | 0
| Design and Engineering |  |  | 4% |  |  | 2543
| Permit, testing and inspection |  |  | 1.25% |  |  | 826
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 66934.737

## LRMF NC Electric Z3 O1
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4500 | 36000
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
55916.737
|  | Subtotal |  |  |  |  | 55916.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5033 | 0
| Design and Engineering |  |  | 4% |  |  | 2438
| Permit, testing and inspection |  |  | 1.25% |  |  | 792
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 64179.737

## LRMF NC Electric Z3 O2
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 6500 | 52000
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
71916.737
|  | Subtotal |  |  |  |  | 71916.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 6473 | 0
| Design and Engineering |  |  | 4% |  |  | 3136
| Permit, testing and inspection |  |  | 1.25% |  |  | 1019
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 82544.737

## LRMF NC Electric Z4 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
4
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4800 | 38400
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
58316.737
|  | Subtotal |  |  |  |  | 58316.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5249 | 0
| Design and Engineering |  |  | 4% |  |  | 2543
| Permit, testing and inspection |  |  | 1.25% |  |  | 826
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 66934.737

## LRMF NC Electric Z4 O2 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
4
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 6500 | 52000
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
71916.737
|  | Subtotal |  |  |  |  | 71916.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 6473 | 0
| Design and Engineering |  |  | 4% |  |  | 3136
| Permit, testing and inspection |  |  | 1.25% |  |  | 1019
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 82544.737

## LRMF NC Electric Z6
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4400 | 35200
|  |  | Ducted mini-split heat pump, fan coil in-unit, 1.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
55116.737
|  | Subtotal |  |  |  |  | 55116.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 4961 | 0
| Design and Engineering |  |  | 4% |  |  | 2403
| Permit, testing and inspection |  |  | 1.25% |  |  | 781
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 63261.737

## LRMF NC Electric Z6 O2
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 5958.3333 | 47666.6667
|  |  | Ducted mini-split heat pump, fan coil in-unit, 1.5-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
67583.4036
|  | Subtotal |  |  |  |  | 67583.4036
0
| General Conditions and Overhead |  |  | 9% |  |  | 6083 | 0
| Design and Engineering |  |  | 4% |  |  | 2947
| Permit, testing and inspection |  |  | 1.25% |  |  | 958
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 77571.4036

## LRMF NC Electric Z9 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
9
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4800 | 38400
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
58316.737
|  | Subtotal |  |  |  |  | 58316.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5249 | 0
| Design and Engineering |  |  | 4% |  |  | 2543
| Permit, testing and inspection |  |  | 1.25% |  |  | 826
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 66934.737

## LRMF NC Electric Z9 O2 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
9
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 6500 | 52000
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
71916.737
|  | Subtotal |  |  |  |  | 71916.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 6473 | 0
| Design and Engineering |  |  | 4% |  |  | 3136
| Permit, testing and inspection |  |  | 1.25% |  |  | 1019
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 82544.737

## LRMF NC Electric Z10
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
10
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 5200 | 41600
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
61516.737
|  | Subtotal |  |  |  |  | 61516.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5537 | 0
| Design and Engineering |  |  | 4% |  |  | 2682
| Permit, testing and inspection |  |  | 1.25% |  |  | 872
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 70607.737
Note on D21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: removed a typo

## LRMF NC Electric Z12 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
12
Demolition
|  | Remove existing furnace |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 5200 | 41600
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
61516.737
|  | Subtotal |  |  |  |  | 61516.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5537 | 0
| Design and Engineering |  |  | 4% |  |  | 2682
| Permit, testing and inspection |  |  | 1.25% |  |  | 872
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 70607.737

## LRMF NC Electric Z12 O2
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
12
Demolition
|  | Remove existing furnace |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 7041.6667 | 56333.3333
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2.5-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
76250.0703
|  | Subtotal |  |  |  |  | 76250.0703
0
| General Conditions and Overhead |  |  | 9% |  |  | 6863 | 0
| Design and Engineering |  |  | 4% |  |  | 3325
| Permit, testing and inspection |  |  | 1.25% |  |  | 1080
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 87518.0703

## LRMF NC Electric Z3 S DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3600 | 28800
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
48716.737
|  | Subtotal |  |  |  |  | 48716.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 4385 | 0
| Design and Engineering |  |  | 4% |  |  | 2124
| Permit, testing and inspection |  |  | 1.25% |  |  | 690
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 55915.737

## LRMF NC Electric Z3 O1 DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3375 | 27000
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
46916.737
|  | Subtotal |  |  |  |  | 46916.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 4223 | 0
| Design and Engineering |  |  | 4% |  |  | 2046
| Permit, testing and inspection |  |  | 1.25% |  |  | 665
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 53850.737

## LRMF NC Electric Z3 O2 DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
3
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4875 | 39000
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
58916.737
|  | Subtotal |  |  |  |  | 58916.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5303 | 0
| Design and Engineering |  |  | 4% |  |  | 2569
| Permit, testing and inspection |  |  | 1.25% |  |  | 835
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 67623.737

## LRMF NC Electric Z6 DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3300 | 26400
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 1.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
46316.737
|  | Subtotal |  |  |  |  | 46316.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 4169 | 0
| Design and Engineering |  |  | 4% |  |  | 2019
| Permit, testing and inspection |  |  | 1.25% |  |  | 656
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 53160.737

## LRMF NC Electric Z6 O2 DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
6
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 4468.75 | 35750
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 1.5-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
55666.737
|  | Subtotal |  |  |  |  | 55666.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5010 | 0
| Design and Engineering |  |  | 4% |  |  | 2427
| Permit, testing and inspection |  |  | 1.25% |  |  | 789
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 63892.737

## LRMF NC Electric Z10 DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
10
Demolition
|  | Remove existing wall furnace, patch & repair |  |  |  |  | Not Required
|  |  | Labor | 32
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 3900 | 31200
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 2.5-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Ductwork |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
51116.737
|  | Subtotal |  |  |  |  | 51116.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 4601 | 0
| Design and Engineering |  |  | 4% |  |  | 2229
| Permit, testing and inspection |  |  | 1.25% |  |  | 724
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 58670.737
Note on D21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: removed a typo

## LRMF NC Electric Z12 O2 DL
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: New Construction
New Construction
Electric Option
12
Demolition
|  | Remove existing furnace |  |  |  |  | Not Required
Labor
Disposal
0
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 5281.25 | 42250
|  |  | Ductless mini-split heat pump, wall-mounted interior unit, 2.5-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 8 | EA | 100 | 800
|  |  | Refrigerant piping and refrigerant | 800 | LF | 4 | 3200
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 96 | HR | 58.8662 | 5651.158
Controls
|  |  | Thermostat & wiring | 8 | EA | 400 | 3200
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 16 | EA | 65 | 1040
|  |  | Panel and main service modification |  |  |  | Not Required
|  |  | Gas supply piping |  |  |  | Not Required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork connections (excludes distributed ductwork) |  |  |  |  | 0
|  |  | Miscellaneous supplies |  |  |  | Included in installation
|  |  | Labor |  |  |  | Included in installation
62166.737
|  | Subtotal |  |  |  |  | 62166.737
0
| General Conditions and Overhead |  |  | 9% |  |  | 5595 | 0
| Design and Engineering |  |  | 4% |  |  | 2710
| Permit, testing and inspection |  |  | 1.25% |  |  | 881
| Contractor Profit/Market Factor | [5 empty] | 0
| Recommended Budget | [5 empty] | 71352.737

## LRMF 90 Electric Z3 S (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 6300 | 37800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 21 SEER/13 EER, 11 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
55303.9475
|  | Subtotal |  |  |  |  | 57216.737
0
| General Conditions and Overhead |  |  | 15% |  |  | 8583 | 0
| Design and Engineering |  |  | 10% |  |  | 6580
| Permit, testing and inspection |  |  | 1.25% |  |  | 905
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 73284.737

## LRMF 90 Electric Z3 O1 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 5200 | 31200
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 14 SEER/12.2 EER, 8.2 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
48703.9475
|  | Subtotal |  |  |  |  | 50616.737
0
| General Conditions and Overhead |  |  | 15% |  |  | 7593 | 0
| Design and Engineering |  |  | 10% |  |  | 5821
| Permit, testing and inspection |  |  | 1.25% |  |  | 800
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 64830.737

## LRMF 90 Electric Z3 O2 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
3
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 6800 | 40800
|  |  | Ducted mini-split heat pump, fan coil in-unit, 2-ton 30 SEER/15 EER, 14 HSPF |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
58303.9475
|  | Subtotal |  |  |  |  | 60216.737
0
| General Conditions and Overhead |  |  | 15% |  |  | 9033 | 0
| Design and Engineering |  |  | 10% |  |  | 6925
| Permit, testing and inspection |  |  | 1.25% |  |  | 952
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 77126.737

## LRMF 90 Electric Z4 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
4
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 5900 | 35400
|  |  | Ducted split heat pump AHU in-unit, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
52903.9475
|  | Subtotal |  |  |  |  | 54816.737
0
| General Conditions and Overhead |  |  | 15% |  |  | 8223 | 0
| Design and Engineering |  |  | 10% |  |  | 6304
| Permit, testing and inspection |  |  | 1.25% |  |  | 867
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 70210.737

## LRMF 90 Electric Z6 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
6
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 5400 | 32400
|  |  | Ducted split heat pump AHU in-unit, 2-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
49903.9475
|  | Subtotal |  |  |  |  | 51816.737
0
| General Conditions and Overhead |  |  | 15% |  |  | 7773 | 0
| Design and Engineering |  |  | 10% |  |  | 5959
| Permit, testing and inspection |  |  | 1.25% |  |  | 819
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 66367.737

## LRMF 90 Electric Z9 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
9
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 5900 | 35400
|  |  | Ducted split heat pump AHU in-unit, 3-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
52903.9475
|  | Subtotal |  |  |  |  | 54816.737
0
| General Conditions and Overhead |  |  | 15% |  |  | 8223 | 0
| Design and Engineering |  |  | 10% |  |  | 6304
| Permit, testing and inspection |  |  | 1.25% |  |  | 867
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 70210.737

## LRMF 90 Electric Z10 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
10
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 6100 | 36600
|  |  | Ducted split heat pump AHU in-unit, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
55516.737
|  | Subtotal |  |  |  |  | 57429.5264
0
| General Conditions and Overhead |  |  | 15% |  |  | 8614 | 0
| Design and Engineering |  |  | 10% |  |  | 6604
| Permit, testing and inspection |  |  | 1.25% |  |  | 908
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 73555.5264

## LRMF 90 Electric Z12 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: 1990's
1990's
Electric Option
12
Demolition
Remove existing furnace
|  |  | Labor | 24 | HR | 58.8662 | 1412.7895
|  |  | Disposal | 1 | LS | 500 | 500
1912.7895
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 6 | EA | 6100 | 36600
|  |  | Ducted split heat pump AHU in-unit, 4-ton 18 SEER/14 EER, 10 HSPF, two-speed |  |  |  | 0
|  |  | Concrete pad, precast | 6 | EA | 100 | 600
|  |  | Refrigerant piping and refrigerant | 600 | LF | 4 | 2400
|  |  | Miscellaneous supplies | 6 | LS | 400 | 2400
|  |  | Labor | 64 | HR | 58.8662 | 3767.4386
Controls
|  |  | Thermostat & wiring | 6 | EA | 400 | 2400
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 12 | EA | 95 | 1140
|  |  | Panel and main service modification |  |  |  | Not required
|  |  | Gas supply piping |  | LF |  | Not required
|  |  | Labor | 48 | HR | 58.8662 | 2825.579
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 6 | LS | 250 | 1500
|  |  | Labor | 32 | HR | 58.8662 | 1883.7193
55516.737
|  | Subtotal |  |  |  |  | 57429.5264
0
| General Conditions and Overhead |  |  | 15% |  |  | 8614 | 0
| Design and Engineering |  |  | 10% |  |  | 6604
| Permit, testing and inspection |  |  | 1.25% |  |  | 908
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 73555.5264

## LRMF 78 Electric Z3 S (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 1500 | 12000
|  |  | Packaged terminal heat pump, 2-ton 11 EER, 3.3 COP, through wall |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
34140.6844
|  | Subtotal |  |  |  |  | 35111.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 5267 | 0
| Design and Engineering |  |  | 10% |  |  | 4038
| Permit, testing and inspection |  |  | 1.25% |  |  | 555
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 44971.6142

## LRMF 78 Electric Z3 O1 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
3
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 1200 | 9600
|  |  | Packaged terminal heat pump, 2-ton 7.6 EER, 2.5 COP |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
31740.6844
|  | Subtotal |  |  |  |  | 32711.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 4907 | 0
| Design and Engineering |  |  | 10% |  |  | 3762
| Permit, testing and inspection |  |  | 1.25% |  |  | 517
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 41897.6142

## LRMF 78 Electric Z4 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
4
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 1800 | 14400
|  |  | Packaged terminal heat pump, 3-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
36540.6844
|  | Subtotal |  |  |  |  | 37511.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 5627 | 0
| Design and Engineering |  |  | 10% |  |  | 4314
| Permit, testing and inspection |  |  | 1.25% |  |  | 593
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 48045.6142

## LRMF 78 Electric Z6 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
6
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 1500 | 12000
|  |  | Packaged terminal heat pump, 2-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
34140.6844
|  | Subtotal |  |  |  |  | 35111.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 5267 | 0
| Design and Engineering |  |  | 10% |  |  | 4038
| Permit, testing and inspection |  |  | 1.25% |  |  | 555
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 44971.6142

## LRMF 78 Electric Z9 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
9
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 1800 | 14400
|  |  | Packaged terminal heat pump, 3-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
36540.6844
|  | Subtotal |  |  |  |  | 37511.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 5627 | 0
| Design and Engineering |  |  | 10% |  |  | 4314
| Permit, testing and inspection |  |  | 1.25% |  |  | 593
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 48045.6142

## LRMF 78 Electric Z10 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
10
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 2200 | 17600
|  |  | Packaged terminal heat pump, 4-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
39740.6844
|  | Subtotal |  |  |  |  | 40711.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 6107 | 0
| Design and Engineering |  |  | 10% |  |  | 4682
| Permit, testing and inspection |  |  | 1.25% |  |  | 644
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 52144.6142

## LRMF 78 Electric Z12 (hidden)
Low Rise Multi-Family | [8 empty] | Low Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
12
Demolition
Remove existing wall furnace, patch & repair
|  |  | Labor | 8 | HR | 58.8662 | 470.9298
|  |  | Disposal | 1 | LS | 500 | 500
970.9298
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | Included in heat pump
New Furnace, equipment price
Heating included in split system heat pump
Miscellaneous supplies
Labor
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 8 | EA | 2200 | 17600
|  |  | Packaged terminal heat pump, 4-ton 11 EER, 3.3 COP |  |  |  | 0
|  |  | Concrete pad, precast |  |  |  | Not required
|  |  | Refrigerant piping and refrigerant |  |  |  | Not required
|  |  | Miscellaneous supplies | 8 | LS | 400 | 3200
|  |  | Labor | 192 | HR | 58.8662 | 11302.3159
Controls
|  |  | Thermostat & wiring | 8 | EA | 200 | 1600
Gas and Electrical Supply
|  |  | New electrical circuits to equipment | 8 | EA | 125 | 1000
|  |  | Panel and main service modification | 1 | EA | 800 | 800
|  |  | Gas supply piping |  |  |  | Not required
|  |  | Labor | 72 | HR | 58.8662 | 4238.3685
Ductwork modifications
|  |  | Miscellaneous supplies |  |  |  | Not required
|  |  | Labor |  |  |  | Not required
39740.6844
|  | Subtotal |  |  |  |  | 40711.6142
0
| General Conditions and Overhead |  |  | 15% |  |  | 6107 | 0
| Design and Engineering |  |  | 10% |  |  | 4682
| Permit, testing and inspection |  |  | 1.25% |  |  | 644
| Contractor Profit/Market Factor |  |  | 0% |  |  | 0
| Recommended Budget | [5 empty] | 52144.6142

## HRMF NC Gas Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Gas Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF NC Electric Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: New Construction
New Construction
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Gas Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 90 Electric Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: 1990's
1990's
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z3 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 3
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z4 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z6 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z9 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z10 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Gas Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Gas Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HRMF 78 Electric Z12 (hidden)
High-Rise Multi-Family | [8 empty] | High-Rise Multi-Family: Pre-1978
Pre-1978
Electric Option
Zone 4, 6, 9, 10, 12
Demolition
Remove existing furnace
|  |  | Labor | 16 | HR | #N/A | #N/A
|  |  | Disposal | 1 | LS | 500 | 500
#N/A
0
| Installation | [5 empty] | 0
|  | Furnace |  |  |  |  | 0
|  |  | New Furnace, equipment price | 1 | EA | 900 | 900
|  |  | Ducted attic furnace 80 AFUE, 40 kBtu/h |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 16 | HR | #N/A | #N/A
|  | Air Conditioner |  |  |  |  | 0
|  |  | New Air Conditioner, equipment price | 1 | EA | 2800 | 2800
|  |  | Split AC 14 SEER/12.2 EER, 2 tons |  |  |  | 0
|  |  | Concrete pad, precast | 1 | EA | 100 | 100
|  |  | Refrigerant piping and refrigerant | 100 | LF | 4 | 400
|  |  | Miscellaneous supplies | 1 | LS | 400 | 400
|  |  | Labor | 32 | HR | #N/A | #N/A
Controls
|  |  | Thermostat & wiring | 1 | EA | 400 | 400
|  | Ductwork modifications |  |  |  |  | 0
|  |  | Miscellaneous supplies | 1 | LS | 250 | 250
|  |  | Labor | 24 | HR | #N/A | #N/A
#N/A
|  | Subtotal |  |  |  |  | #N/A
0
| General Conditions and Overhead |  |  | #N/A |  |  | #N/A | 0
| Design and Engineering |  |  | #N/A |  |  | #N/A
| Contractor Profit/Market Factor |  |  | #N/A |  |  | #N/A
| Recommended Budget | [5 empty] | #N/A
cell 37 check

## HVAC (hidden)
HVAC
|  |  | Zone | Existing |  | Gas Technology |  | Electric tech
Single Family
|  | New Construction | 3 | - | - | Ducted Furnace | no AC | Ducted Split Heat Pump
|  |  | 6, 4, 9, 10, 12 | - | - | Ducted Furnace | Split AC | Ducted Split Heat Pump
|  | 1990's | 3, 6 | Ducted Furnace | No AC | New Furnace | AC | Ducted Split Heat Pump
|  |  | 4, 9, 10, 12 | Ducted Furnace | Split AC | New Furnace | AC | Ducted Split Heat Pump
|  | Pre 1978 | 3, 6 | Wall Furnace | No AC | New Ducted Furnace, addition of ducts | AC | Non-ducted MSHP, Multi-head
|  |  | 4, 9 | Wall Furnace | Window AC | New Furnace, addition of ducts |  | Non-ducted MSHP, Multi-head
|  |  | 10, 12 | Ducted Furnace | Split AC | New Furnace | AC | Ducted Split Heat Pump
Low-Rise Multi-Family
|  | New Construction | 3 | - | - | Ducted Furnace | no AC | New Ducted mini-split heat pump
|  |  | 6, 4, 9, 10, 12 | - | - | Ducted Furnace | Split AC | New Ducted mini-split heat pump
|  | 1990's | 3, 6 | Combined Hydronic | No AC | Combined hydronic | Split AC | Ducted Split Heat Pump
|  |  | 4, 9, 10, 12 | Combined Hydronic | Split AC | Combined hydronic | Split AC | Ducted Split Heat Pump
|  | Pre 1978 | 3, 6 | Wall Furnace | No AC | New Wall Furnace | Window AC | Packaged Thermal Heat Pump
|  |  | 4, 9 | Wall Furnace | Window AC | New Wall Furnace | Window AC | Packaged Thermal Heat Pump
High-Rise Multi-Family
|  | New Construction | 3 | - | - | Hydronic Heating only FCU, Central Condensing Gas Boiler | No AC | Electric Resistance + ERV | No AC
|  |  | 6, 4, 9, 10, 12 | - | - | In-unit 4-pipe fan coil units connected to central natural gas boiler and chiller/cooling towers |  | VRF
|  | 1990's | 3 | Hydronic Heating only FCU, Central Gas Boiler | No AC | Update with new combined gas boiler | No AC
|  |  | 6, 4, 9, 10, 12 | In-unit 4-pipe fan coil units connected to central condensing gas boiler and existing chiller/cooling towers |  | Keep existing system with updated condensing gas boiler and existing chiller/coolant towers |  | Keep existing system, replace boiler with ASHP water heater, keep existing chiller/cooling tower
|  | Pre 1978 | 3 | Hydronic radiators, central gas boiler | No AC | Update with new condensing gas boiler | No AC | Keep existing system, replace boiler with new central AHP | No AC
|  |  | 6, 4, 9, 10, 12 | Hydronic radiators, central gas boiler | Window AC | Keep hydronic radiators, update central gas boiler with condensig gas boiler | Window AC | Abandon prior heating system and replace AC unit with PTHP for heating and cooling