## Dashboard
Refrigerant Avoided Cost Calculator
For the California Public Utilities Commission
Use this calculator to calculate the avoided costs of refrigerant leakage for devices containing a refrigerant, when refrigerant type or amount is changed or a device is replaced early.
This calculator can be used to calculate the avoided cost compared to a counterfactual for three measure types including:
1) Normal Replacement Measure, where a device is replaced by a new device at the end of its useful life
2) Add-on Equipment Measure, where a new piece of equipment is installed alongside existing equipment
3) Accelerated Replacement Measure, where an existing device is retired early and replaced with a new device
For Normal Replacement and Add-on Equipment Measures, it is assumed that the existing equipment is the same between the measure and counterfactual case, and thus does not need to be specified by the user measure
since it does not contribute to the relative avoided costs. However, if Accelerated Replacement is chosen as the measure type, both new and existing device inputs must be specified to calculate avoided costs. For Accelerated Replacement
measures, it is assumed that the existing device and refrigerant are the same between the measure and the counterfactual case. However, in the counterfactual case, the existing device is retired at the end of its useful life.
Note that the output field is labeled "NPV avoided costs" regardless of whether that value represents a benefit or a cost, so users must be careful to input this data correctly into their cost-effectiveness tools.
Please note that, for fuel substitution measures, it is critical to take into account the avoided cost of refrigerant leakage from air conditioners, if the building(s) in question would have had an air conditioner in the absence of the measure.
For example, if a heat pump replaces both a natural gas heater and an air conditioner, the reduction in refrigerant leakage from this replaced air conditioner must be considered in any cost-effectiveness calculations.
If the replacement of an existing or planned air conditioner is not reflected, the net cost of refrigerant leakage from fuel substitution measures could be seriously over-estimated.
User Dashboard
| Inputs | [6 empty] | Result
[8 empty] | NPV Avoided Costs in Measure Start Year (2020$) |  |  | Cell Color Coding
| Measure type | Normal Replacement or Add-on Equipment | [5 empty] | 429.014 |  |  | Input Value
Dropdown List
|  | Measure |  |  | Counterfactual | [5 empty] | Calculated Input
|  | New Device | Existing Device |  | New Device | Existing Device |  |  |  |  | Lookup Formula
| Device Type (see Refrigerant Leakage tab for list of devices) | Residential Heat Pumps | Residential Heat Pumps |  | Residential Heat Pumps | Residential Heat Pumps |  |  |  |  | Final Outputs
Measure Lifetime Highlighted in Calculations
ARB average
User Specified
CARB database
| Use ARB average device lifetime or user-specified? | ARB average | ARB average |  | ARB average | ARB average
| User-specified device lifetime (yr) (applicable for user-specified lifetime) | 2 | 10 |  | 2 | 10
| Device lifetime (yr) | 15 | 0 |  | 15 | 0
| Device installation year | 2025 | 2022 |  | 2025 | 2022
| Device retirement year | 2039 | 2021 |  | 2039 | 2021
| Number of years device was retired early | 0 | 0 |  | 0 | 0
| Use ARB average refrigerant charge or user-specified? | ARB average | ARB average |  | ARB average | ARB average
| User-specified device refrigerant charge (lb) (applicable for user-specified charge) | 7.5 | 7.5 |  | 7.5 | 7.5
| Active device refrigerant charge (lb) | 8.2 | 8.2 |  | 8.2 | 8.2 | [6 empty] | PG&E
SCE
| Device refrigerant used (see Refrigerang GWPs tab for list of refrigerants) | HFC-134a | THR-03 |  | R-410A | THR-03 | [6 empty] | SDG&E
| User-specified refrigerant GWP (applicable for user-specified refrigerant) | 675 | 1000 |  | 675 | 1000 | [6 empty] | User-specified
| Measure start year | 2025
| Measure end year | 2039
| WACC selection | PG&E
| User-specified WACC (%) | 10%
| Active WACC (%) | 7.34%
| GWP time horizon (100-yr is default) | 100-yr
Calculations:
|  | Measure |  |  | Counterfactual |  |  |  | Conversions
| Intermediate Calculations | New Device | Existing Device |  | New Device | Existing Device |  |  |  | 2204.62 | lb
| Start year | 2025 | 2022 |  | 2025 | 2022 |  |  | = | 1 | metric ton
| End year | 2039 | 2021 |  | 2039 | 2021
| Number of device lifetime years overlapping with measure years | 15 | 0 |  | 15 | 0
| % of device lifetime occuring during measure years | 100% | 0% |  | 100% | 0%
| % of device lifetime retired early | 0% | 0% |  | 0% | 0%
| Refrigerant GWP | 1430 | 954 |  | 2087.5 | 954
| Annual refrigerant leakage % | 5.3% | 5.3% |  | 5.3% | 5.3%
| EOL refrigerant leakage % | 80% | 80% |  | 80% | 80%
| t_EOL | 3 | 3 |  | 3 | 3
| Annual leakage (tonnes CO2e) | 0.2819 | 0 |  | 0.41151 | 0
| End-of-life leakage (tonnes CO2e) | 3.5785 | 0 |  | 5.2239 | 0
|  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Measure | New device annual refrigerant leakage during measure life (tonnes CO2e) |  | 0 | 0 | 0 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Existing device annual refrigerant leakage during measure life (tonnes CO2e) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New device end-of-life refrigerant leakage (tonnes CO2e) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Existing device end-of-life refrigerant leakage (tonnes CO2e) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2 cost (nominal $/tonne CO2) |  | 131.7984 | 141.7141 | 152.3757 | 163.8394 | 176.1656 | 189.4192 | 203.6698 | 218.9925 | 235.4681 | 253.1831 | 272.2309 | 292.7118 | 314.7335 | 338.4119 | 363.8718 | 391.2471 | 420.6819 | 452.3312 | 486.3616 | 522.9522 | 562.2956 | 604.599 | 650.085 | 698.993 | 751.5806 | 808.1245 | 868.9224 | 934.2943 | 1004.5844 | 1080.1626 | 1161.4269
| Cost from new device annual refrigerant leakage during measure life (nominal $) |  | 0 | 0 | 0 | 46.186 | 49.6607 | 53.3969 | 57.4141 | 61.7336 | 66.378 | 71.3718 | 76.7414 | 82.5149 | 88.7227 | 95.3976 | 102.5747 | 110.2918 | 118.5894 | 127.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost from existing device annual refrigerant leakage during measure life (nominal $) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost from new device end-of-life leakage (nominal $) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1618.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost from existing device end-of-life leakage (nominal $) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from new device annual refrigerant leakage during measure life (2020$) |  | 0 | 0 | 0 | 40.3765 | 39.6524 | 38.9413 | 38.243 | 37.5572 | 36.8836 | 36.2222 | 35.5726 | 34.9347 | 34.3082 | 33.6929 | 33.0887 | 32.4953 | 31.9125 | 31.3402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from existing device annual refrigerant leakage during measure life (2020$) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from new device end-of-life leakage (2020$) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.8435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from existing device end-of-life leakage (2020$) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Counterfactual | New device annual refrigerant leakage during measure life (tonnes CO2e) |  | 0 | 0 | 0 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0.41151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Existing device annual refrigerant leakage during measure life (tonnes CO2e) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New device end-of-life refrigerant leakage (tonnes CO2e) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Existing device end-of-life refrigerant leakage (tonnes CO2e) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2 cost (nominal $/tonne CO2) |  | 131.7984 | 141.7141 | 152.3757 | 163.8394 | 176.1656 | 189.4192 | 203.6698 | 218.9925 | 235.4681 | 253.1831 | 272.2309 | 292.7118 | 314.7335 | 338.4119 | 363.8718 | 391.2471 | 420.6819 | 452.3312 | 486.3616 | 522.9522 | 562.2956 | 604.599 | 650.085 | 698.993 | 751.5806 | 808.1245 | 868.9224 | 934.2943 | 1004.5844 | 1080.1626 | 1161.4269
| Cost from new device annual refrigerant leakage during measure life (nominal $) |  | 0 | 0 | 0 | 67.4219 | 72.4943 | 77.9482 | 83.8126 | 90.1181 | 96.8979 | 104.1879 | 112.0263 | 120.4544 | 129.5166 | 139.2606 | 149.7376 | 161.0028 | 173.1156 | 186.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost from existing device annual refrigerant leakage during measure life (nominal $) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost from new device end-of-life leakage (nominal $) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2362.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost from existing device end-of-life leakage (nominal $) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from new device annual refrigerant leakage during measure life (2020$) |  | 0 | 0 | 0 | 58.9412 | 57.8842 | 56.8462 | 55.8267 | 54.8256 | 53.8424 | 52.8768 | 51.9285 | 50.9973 | 50.0827 | 49.1846 | 48.3025 | 47.4363 | 46.5856 | 45.7502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from existing device annual refrigerant leakage during measure life (2020$) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from new device end-of-life leakage (2020$) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.7681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measure start year PV cost stream from existing device end-of-life leakage (2020$) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NPV Costs
|  |  | Measure | Counterfactual
| NPV cost from new device annual refrigerant leakage during measure life (2020$) |  | 2022: 535.2212; 2023: 781.3107
| NPV cost from existing device annual refrigerant leakage during measure life (2020$) |  | 2022: 0; 2023: 0
| NPV cost from new device end-of-life refrigerant leakage* (2020$) |  | 2022: 397.8435; 2023: 580.7681
| NPV cost from existing device end-of-life refrigerant leakage* (2020$) |  | 2022: 0; 2023: 0
| Total NPV cost with respect to measure start year (2020$) |  | 2022: 933.0648; 2023: 1362.0788
*NPV cost from end-of-life leakage is scaled based on how much of the device lifetime occurred during the measure lifetime and how early the device was retired relative to its effective useful life
Total NPV Avoided Cost (2020$)
429.014
Note on C36: Jen Cardona: User-specified device lifetime should be used if at all possible, since the ARB average represents a wide range of devices.
Note on D59: Gabe Mantegna: 100-yr GWP is default value adopted by Commission. 20-yr GWP is an option for sensitivity analysis.

## ACC Inputs
GHG Value from Natural Gas ACC
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
| $/tonne (nominal) | 122.5766 | 131.7984 | 141.7141 | 152.3757 | 163.8394 | 176.1656 | 189.4192 | 203.6698 | 218.9925 | 235.4681 | 253.1831 | 272.2309 | 292.7118 | 314.7335 | 338.4119 | 363.8718 | 391.2471 | 420.6819 | 452.3312 | 486.3616 | 522.9522 | 562.2956 | 604.599 | 650.085 | 698.993 | 751.5806 | 808.1245 | 868.9224 | 934.2943 | 1004.5844 | 1080.1626 | 1161.4269
Measure Types |  | GHG Value from Natural Gas ACC 2022: IOU WACC (Nominal, after-tax)
Normal Replacement or Add-on Equipment |  | GHG Value from Natural Gas ACC 2021: PG&E; GHG Value from Natural Gas ACC 2022: 7.34%
Accelerated Replacement |  | GHG Value from Natural Gas ACC 2021: SCE; GHG Value from Natural Gas ACC 2022: 7.68%
|  | SDG&E | 7.55%

## Refrigerant Leakage
Sector | Device type | Average lifetime (years) | Average charge size (amount of refrigerant) in lbs. per unit | Average annual leak rate (q_ann) | Average end-of-life loss rate of remaining refrigerant (q_EOL) | Number of years prior to EOL with no "top-off" refrigerant added to replace full charge (t_EOL) | Percentage of refrigerant charge lost during lifetime | Mass of refrigerant lost during lifetime for average unit (lbs)
Stationary Refrigeration | Large retail food refrigeration 2,000 lbs. + | 15 | 3352 | 24.2% | 20% | 0 | 383% | 12838.16
| Medium retail food refrigeration 200-2,000 lbs. | 15 | 684 | 22.9% | 20% | 0 | 363.5% | 2486.34
| Small retail food refrigeration 50-200 lbs. | 20 | 103 | 15.6% | 20% | 0 | 332% | 341.96
| Sub-small retail food refrigeration < 50 lbs. | 14 | 23 | 15% | 34% | 0 | 244% | 56.12
| Large commercial refrigeration 2,000 lbs. + | 15 | 3352 | 24.2% | 20% | 0 | 383% | 12838.16
| Medium commercial refrigeration 200-2,000 lbs. | 15 | 684 | 22.9% | 20% | 0 | 363.5% | 2486.34
| Small commercial refrigeration 50-200 lbs. | 20 | 103 | 15.6% | 20% | 0 | 332% | 341.96
| Sub-small commercial refrigeration < 50 lbs. | 14 | 23 | 15% | 34% | 0 | 244% | 56.12
| Large cold storage 2,000 lbs. + | 20 | 7252 | 14.8% | 20% | 0 | 316% | 22916.32
| Medium cold storage 200-2,000 lbs. | 20 | 552 | 10.3% | 20% | 0 | 226% | 1247.52
| Small cold storage 50-200 lbs. | 20 | 113 | 4% | 20% | 0 | 100% | 113
| Large industrial process cooling 2,000 lbs. + | 20 | 5873 | 12.3% | 20% | 0 | 266% | 15622.18
| Medium industrial process cooling 200-2,000 lbs. | 20 | 660 | 12.5% | 20% | 0 | 270% | 1782
| Small industrial process cooling 50-200 lbs. | 20 | 104 | 9.1% | 20% | 0 | 202% | 210.08
| Stand alone (self-contained) refrig units | 20 | 1.023 | 1% | 98.5% | 10 | 108.7% | 1.1115
| Refrigerated Food Processing and Dispensing Equipment | 12 | 3 | 1% | 98.5% | 6 | 104.6% | 3.1377
| Commercial Ice Machines | 5 | 3.31 | 0.5% | 98.5% | 5 | 98.54% | 3.2616
| Water Coolers - Drinking Fountains | 14 | 0.25 | 1% | 98.5% | 14 | 98.71% | 0.24677
| Refrigerated vending machines | 15 | 0.63 | 1% | 98.5% | 15 | 98.72% | 0.62197
| Heat Pump Water Heaters | 14 | 2.4 | 1% | 100% | 14 | 100% | 2.4
| Heat Pump Clothes Dryers | 14 | 0.882 | 1% | 100% | 14 | 100% | 0.882
| Household refrigerator freezer | 14 | 0.342 | 1% | 77% | 14 | 80.22% | 0.27435
Stationary Air-conditioning | Large Chiller 2,000 lbs. + | 20 | 3978 | 2.3% | 20% | 0 | 66% | 2625.48
| Medium Chiller 200-2,000 lbs. | 20 | 526 | 3% | 20% | 0 | 80% | 420.8
| Commercial Unitary AC 50-200 lbs., > 135,000 BTUh size | 20 | 70 | 7% | 20% | 0 | 160% | 112
| Commercial Unitary AC, < 50-lbs., < 135,000 BTUh size (includes smaller "residential-type" central AC and heat pumps) | 15 | 18.2 | 4.7% | 56% | 0 | 126.5% | 23.023
| Window/Room AC and PTAC Units, commercial | 12 | 1.54 | 2% | 98.5% | 12 | 98.86% | 1.5224
| Residential Unitary AC | 15 | 7.5 | 5% | 80% | 3 | 143% | 10.725
| Residential Heat Pumps | 15 | 8.2 | 5.3% | 80% | 3 | 146.8% | 12.036
| Window/Room/Wall AC and Packaged Terminal AC (PTAC) Units, residential | 12 | 1.54 | 2% | 98.5% | 12 | 98.86% | 1.5224
| Portable AC | 10 | 1.54 | 1% | 98.5% | 10 | 98.65% | 1.5192
| Dehumidifiers | 5 | 1 | 1% | 98.5% | 5 | 98.58% | 0.98575
MVAC and Transport Refrigeration | Mobile Vehicle AC (MVAC) Light Duty (LD) | 12 | 1.52 | 8% | 42.5% | 2 | 131.7% | 2.0018
| MVAC Heavy Duty (HD) (non-bus) | 10 | 2.92 | 33.8% | 51.34% | 1 | 372% | 10.862
| MVAC Bus | 12 | 21.8 | 11.7% | 49% | 1 | 183.7% | 40.0394
| MVAC Off-Road | 10 | 2.43 | 33.8% | 51.3% | 1 | 372% | 9.0386
| Transport Refrigerated Units (TRUs) | 7 | 16 | 15% | 49% | 1 | 146.6% | 23.464
| Refrigerated Shipping Containers | 5 | 33.1 | 5% | 19.1% | 1 | 43.15% | 14.281
| Ships | 15 | 273.2 | 36.6% | 0% | 1 | 549% | 1499.868
No device | None | 0 | 0 | 0% | 0% | 0 | 0% | 0
Note on A1: Gabe Mantegna: This tab copied from ACC.
Note on H1: Microsoft Office User: Primary values for use from this tab. Equal to (q_ann,i * t_i + q_EOL,i * (1 - q_ann,i * t_EOL,i)) in documentation
Note on I1: Microsoft Office User: Illustrative only. Must use actual refrigerant charge for calculations

## Refrigerant GWPs
Common name of refrigerant/GHG | Full Name | Atmospheric Life Time in Years | 100-year GWP Values from IPCC Fourth Assessment Report (AR4) (2007) | 20-year GWP Values from IPCC Fourth Assessment Report (AR4) (2007) | Notes | Active GWP
CFC-11 | Trichlorofluoromethane (CCl3F) | 45 | 4750 | 6730 | Controlled by Montreal Protocol; not included in ARB inventory by international convention | 4750
CFC-12 | Dichlorodifluoromethane (CCl2F2) | 100 | 10900 | 11000 |  | 10900
CFC-13 | Chlorotrifluoromethane (CClF3) | 640 | 14400 | 10800 |  | 14400
CFC-113 | 1,1,2-Trichlorotrifluoroethane (C2F3Cl3) | 85 | 6130 | 6540 |  | 6130
CFC-114 | Dichlorotetrafluoroethane (C2F4Cl2) | 190 | 10000 | 8040 |  | 10000
CFC-115 | Monochloropentafluoroethane (C2F5Cl) | 1020 | 7370 | 5310 |  | 7370
Halon 1211 | Bromochlorodifluoromethane (CF2ClBr) | 16 | 1890 | 4750 |  | 1890
Halon 1301 | Bromotrifluoromethane (CF3Br) | 65 | 7140 | 8480 |  | 7140
Halon 2402 | Dibromotetrafluoroethane (C2F4Br2) | 20 | 1640 | 3680 |  | 1640
Carbon tetrachloride | Carbon tetrachloride (CCl4) | 26 | 1400 | 2700 |  | 1400
Methyl bromide | Methyl bromide (CH3Br) | 0.8 | 5 | 17 |  | 5
Methyl chloroform (R-140a) | 1,1,1-trichloroethane (C2H3Cl3) | 5 | 146 | 506 |  | 146
Methylene chloride | Dichloromethane (CH2Cl2) | 0.38 | 8.7 | 31 |  | 8.7
HCFC-21 | Dichlorofluoromethane (CHFCl2) | 1.7 | 148 | 543 |  | 148
HCFC-22 | Monochlorodifluoromethane (CHClF2) | 11.9 | 1810 | 5160 |  | 1810
HCFC-123 | Dichlorotrifluoroethane (C2HF3Cl2) | 1.3 | 77 | 273 |  | 77
HCFC-124 | Monochlorotetrafluoroethane (C2HF4Cl) | 5.9 | 609 | 2070 |  | 609
HCFC-141b | Dichlorofluoroethane (C2H3FCl2) | 9.2 | 725 | 2250 |  | 725
HCFC-142b | Monochlorodifluoroethane (C2H3F2Cl) | 17.2 | 2310 | 5490 |  | 2310
HCFC-225ca | Dichloropentafluoropropane (C3HF5Cl2) | 1.9 | 122 | 429 |  | 122
HCFC-225cb | Dichloropentafluoropropane (CHClFCF2CClF2) | 5.9 | 595 | 2030 |  | 595
Carbon Dioxide | Carbon Dioxide (CO2) | 50-200 | 1 | 1 |  | 1
Methane | Methane (CH4) | 12 | 25 | 72 |  | 25
Nitrous Oxide | Nitrous Oxide (N2O) | 114 | 298 | 289 |  | 298
HFC-23 | Trifluoromethane (CHF3) | 260 | 14800 | 12000 |  | 14800
HFC-32 | Difluoromethane (CH2F2) | 5 | 675 | 2330 |  | 675
HFC-125 | Pentafluoroethane (C2HF5) | 29 | 3500 | 6350 |  | 3500
HFC-134a | 1,1,1,2-Tetrafluoroethane (CH2FCF3) | 13.8 | 1430 | 3830 |  | 1430
HFC-143a | 1,1,1-Trifluoroethane (C2H3F3) | 52 | 4470 | 5890 |  | 4470
HFC-152a | 1,1-Difluoroethane (C2H4F2) | 1.4 | 124 | 437 |  | 124
HFC-161 | Fluoroethane [ethyl fluoride] (CH3CH2F) | 0.25 | Not Available | Not Available |  | Not Available
HFC-227ea | 1,1,1,2,3,3,3-Heptafluoropropane (C3HF7) | 33 | 3220 | 5310 |  | 3220
HFC-236fa | 1,1,1,3,3,3-hexafluoropropane (C3H2F6) | 220 | 9810 | 8100 |  | 9810
HFC-245fa | 1,1,1,3,3-pentafluoropropane (C3H3F5) | 7.2 | 1030 | 3380 |  | 1030
HFC-365mfc | 1,1,1,3,3-pentafluorobutane (C4H5F5) | 9.9 | 794 | 2520 |  | 794
HFC-43-10mee | 1,1,1,2,2,3,4,5,5,5-decafluoropentane (C5H2F10) | 15 | 1640 | 4140 |  | 1640
HFE-7100 | HFE-449s1 (C4F9OCH3) | 5 | 390 | 1040 |  | 390
HFE-7200 | HFE-569sf2 (C4F9OC2H5) | 0.77 | 55 | 207 |  | 55
HFE-8200 | blend ethyl nonafluoroisobutyl ether and ethyl nonafluorobutyl ether | 0.77 | 55 | Not Available |  | 55
PFC-14 | Tetrafluoromethane (CF4) | 50000 | 7390 | 5210 |  | 7390
PFC-116 | Hexafluoroethane (C2F6) | 10000 | 12200 | 8630 |  | 12200
PFC-218 | Octafluoropropane (C3F8) | 2600 | 8830 | 6310 |  | 8830
PFC-318 | Perfluorocyclobutane (C4F8) | 3200 | 10300 | 7310 |  | 10300
PFC-31-10 | Perfluorobutane (C4F10) | 2600 | 8860 | 6330 |  | 8860
PFC-41-12 | Perfluoropentane (C5F12) | 4100 | 9160 | 6510 |  | 9160
PFC-51-14 | Perfluorohexane (C6F14) | 3200 | 9300 | 6600 |  | 9300
PFC-91-18 | Perfluorodecalin (C10F18) | >1000 | >7500 | >5500 |  | >7500
SF6 Sulphur Hexafluoride | Sulphur Hexafluoride (SF6) | 3200 | 22800 | 16300 |  | 22800
NF3 Nitrogen Trifluoride | Nitrogen Trifluoride (NF3) | 740 | 17200 | 12300 |  | 17200
SO2F2 Sulfuryl fluoride | Sulfuryl fluoride (SO2F2) | 36 | Not Available | Not Available |  | Not Available
Trifluoromethyl sulfur pentafluoride | Trifluoromethyl sulfur pentafluoride (SF5CF3) | 800 | 17700 | Not Available |  | 17700
Trifluoromethyl iodide (CF3I) | Trifluoromethyl iodide (CF3I), trifluoroiodomethane | 0.005 | 1 | 1 |  | 1
Dimethyl ether (DME) | Dimethyl ether (DME) (CH3OCH3 (C2H6O)) | 0.005 | 1 | 1 |  | 1
FOR12A | HFC-134a 1,1,1,2-Tetrafluoroethane 80%; HFC-152a 1,1-Difluoroethane 4%; CF3I (Trifluoroiodomethane) 11% |  | 1221 | Not Available |  | 1221
FOR12B | HFC-134a 1,1,1,2-Tetrafluoroethane 77%; Dimethyl ether (DME) (C2H6O) 2%; CF3I (Trifluoroiodomethane) 21% |  | 1101 | Not Available |  | 1101
Freeze 12 | HCFC-142b Monochlorodifluoroethane 20%; HFC-134a 1,1,1,2-Tetrafluoroethane 80% |  | 1606 | Not Available |  | 1606
Free Zone | HCFC-142b Monochlorodifluoroethane 19%; HFC-134a 1,1,1,2-Tetrafluoroethane 79% |  | 1568.6 | Not Available |  | 1568.6
FRIGC FR-12 | HCFC-124 2-Chloro-1,1,1,2-Tetrafluoroethane 39%; HFC-134a 1,1,1,2-Tetrafluoroethane 59%; n-Butane 2% |  | 1081.29 | Not Available |  | 1081.29
G2018C | HCFC-22 Chlorodifluoromethane 95.5%; HFC-152a 1,1-Difluoroethane 1.5%; Propylene R-1270 3% |  | 1730.5 | Not Available |  | 1730.5
GHG-HP | HCFC-22 Chlorodifluoromethane 65%; HCFC-142B Monochlorodifluoroethane 31% Isobutane R-600a 4% |  | 1892.72 | Not Available |  | 1892.72
GHG-X5 | HCFC-22 Chlorodifluoromethane 41%; HCFC-142B Monochlorodifluoroethane 15%; HFC-227ea 1,1,1,2,3,3,3-Heptafluoropropane 40% Isobutane R-600a 4% |  | 2376.72 | Not Available |  | 2376.72
Hot Shot 2 | HFC-134a 1,1,1,2-Tetrafluoroethane 78.8%; HFC-125 Pentafluoroethane 19.5%; R-600a (Isobutane) 1.7% |  | 1809.425 | 4256.341 |  | 1809.425
Ikon A | HFC-152a (unknown %); CF3I (trifluoroiodomethane) (unknown %) |  | 124 | 437 |  | 124
Ikon B | HFC-134a (unknown %); HFC-152a (unknown %); CF3I (trifluoroiodomethane) (unknown %) |  | Not Available | Not Available |  | Not Available
Isceon MO89 | HFC-125 Pentafluoroethane 86%; PFC-218 Octafluoropropane 9%; Propane (R-290) 5% |  | 3141.1255 | 6029.065 |  | 3141.1255
NARM-502 | HCFC-22 Chlorodifluoromethane 90%; HFC-23 Trifluoromethane 5%; HFC-152a 1,1-Difluoroethane 5% |  | 2375.2 | 5265.85 |  | 2375.2
R-401A | HCFC-22 Chlorodifluoromethane 53%; HCFC-124 2-Chloro-1,1,1,2-Tetrafluoroethane 34%; HFC-152a 1,1-Difluoroethane 13% |  | 1182.48 | 3495.41 |  | 1182.48
R-401B | HCFC-22 Chlorodifluoromethane 61%; HCFC-124 2-Chloro-1,1,1,2-Tetrafluoroethane 28%; HFC-152a 1,1-Difluoroethane 11% |  | 1288.26 | 3775.27 |  | 1288.26
R-401C | HCFC-22 Chlorodifluoromethane 33%; HCFC-124 2-Chloro-1,1,1,2-Tetrafluoroethane 52%; HFC-152a 1,1-Difluoroethane 15% |  | 932.58 | 2844.75 |  | 932.58
R-402A | HCFC-22 Chlorodifluoromethane 38%; HFC-125 Pentafluoroethane 60%; Propane (R-290) 2% |  | 2788 | 5770.866 |  | 2788
R-402B | HCFC-22 Chlorodifluoromethane 60%; HFC-125 Pentafluoroethane 38%; Propane (R-290) 2% |  | 2416 | 5509.066 |  | 2416
R-403B | HCFC-22 Chlorodifluoromethane 56%; PFC-218 Octafluoropropane 39%; Propane (R-290) 5% |  | 4458 | 5350.665 |  | 4458
R-404A | HFC-125 Pentafluoroethane 44%; HFC-134a 1,1,1,2-Tetrafluoroethane 4% HFC-143a 1,1,1-Trifluoroethane 52% | 52 years (143a); 29 years (125); 14.6 years (134a) | 3921.6 | 6010 |  | 3921.6
R-406A | HCFC-22 Chlorodifluoromethane 55%; HCFC-142B Monochlorodifluoroethane 41% Isobutane R-600a 4% |  | 1942.72 | 5089.02 |  | 1942.72
R-407A | HFC-32 Difluoromethane 20%; HFC-125 Pentafluoroethane 40%; HFC-134a 1,1,1,2-Tetrafluoroethane 40% | 29 years (R-125); 4.9 years (R-32) | 2107 | 4538 |  | 2107
R-407B | HFC-32 Difluoromethane 10%; HFC-125 Pentafluoroethane 70%; HFC-134a 1,1,1,2-Tetrafluoroethane 20% |  | 2245 | 4494 |  | 2245
R-407C | HFC-32 Difluoromethane 23%: HFC-125 Pentafluoroethane 25%; HFC-134a 1,1,1,2-Tetrafluoroethane 52% |  | 1773.85 | 4115 |  | 1773.85
R-407D | HFC-32 Difluoromethane 15%: HFC-125 Pentafluoroethane 15%; HFC-134a 1,1,1,2-Tetrafluoroethane 70% |  | 1627.25 | 3983 |  | 1627.25
R-407F | HFC-32 Difluoromethane 30%: HFC-125 Pentafluoroethane 30%; HFC-134a 1,1,1,2-Tetrafluoroethane 40% |  | 1824.5 | 4136 |  | 1824.5
R-407H | HFC-32 Difluoromethane 32.5%: HFC-125 Pentafluoroethane 15.0%; HFC-134a 1,1,1,2-Tetrafluoroethane 52.5% |  | 1495.125 | 3720.5 |  | 1495.125
R-408A | HCFC-22 Chlorodifluoromethane 47%; HFC-125 Pentafluoroethane 7%; HFC-143A 1-1-1 Trifluoroethane 46% |  | 3151.9 | 5579.1 |  | 3151.9
R-409A | HCFC-22 Chlorodifluoromethane 60%; HCFC-124 2-Chloro-1,1,1,2-Tetrafluoroethane 25%; HCFC-142b 1-Chloro-1,1-Difluoroethane 15% |  | 1585 | 4437 |  | 1585
R-410A | HFC-32 Difluoromethane 50%; HFC-125 Pentafluoroethane 50% | 29 years (R-125); 4.9 years (R-32) | 2087.5 | 4340 |  | 2087.5
R-410B | HFC-32 Difluoromethane 45%; HFC-125 Pentafluoroethane 55% | 29 years (R-125); 4.9 years (R-32) | 2228.75 | 4541 |  | 2228.75
R-411A | HCFC-22 Chlorodifluoromethane 87.5%; HFC-152a 1,1-Difluoroethane 11%; Propylene R-1270 1.5% |  | 1597.435 | 4563.115 |  | 1597.435
R-411B | HCFC-22 Chlorodifluoromethane 94%; HFC-152a 1,1-Difluoroethane 3%; Propylene R-1270 3% |  | 1705.21 | 4863.6 |  | 1705.21
R-413A | HFC-134a 1,1,1,2-Tetrafluoroethane 88%; PFC-218 Octafluoropropane 9%; Isobutane 3% |  | 2053 | 3938.45 |  | 2053
R-414A | HCFC-22 Chlorodifluoromethane 51%; HCFC-124 Monochlorotetrafluoroethane 39%; HCFC-142b Monochlorodifluoroethane 6%; R-600a Isobutane (hydrocarbon) 4% |  | 1478 | 3768.42 |  | 1478
R-414B | HCFC-22 Chlorodifluoromethane 50%; HCFC-124 Monochlorotetrafluoroethane 39%; HCFC-142b Monochlorodifluoroethane 9.5%; R-600a Isobutane (hydrocarbon) 1.5% |  | 1362 | 3898.545 |  | 1362
R-416A | HFC-134a 1,1,1,2-Tetrafluoroethane 59%; HCFC-124 1-Chloro-1,2,2,2-tetrafluoroethane 39.5%; R-600a Isobutane (hydrocarbon) 1.5% |  | 1084.3 | 3077.395 |  | 1084.3
R-417A | HFC-134a 1,1,1,2-Tetrafluoroethane 50%; HFC-125 Pentafluoroethane 46.6%; Butane 3.4% |  | 2346.102 | 4874.202 |  | 2346.102
R-417B | HFC-125 Pentafluoroethane 79%; HFC-134a 1,1,1,2-Tetrafluoroethane 18.25%; R-600 Butane 2.75% |  | 3026.0575 | 5715.5575 |  | 3026.0575
R-417C | HFC-134a 1,1,1,2-Tetrafluoroethane 78.8%; HFC-125 Pentafluoroethane 19.5%; R-600a (Isobutane) 1.7% |  | 1809.408 | 4256.375 |  | 1809.408
R-420A | HCFC-142b Monochlorodifluoroethane 12%; HFC-134a 1,1,1,2-Tetrafluoroethane 88% |  | 1535.6 | 4029.2 |  | 1535.6
R-421A | HFC-125 Pentafluoroethane 58% HFC-134a 1,1,1,2-Tetrafluoroethane 42% |  | 2630.6 | 5291.6 |  | 2630.6
R-421B | HFC-125 Pentafluoroethane 85% HFC-134a 1,1,1,2-Tetrafluoroethane 15% |  | 3189.5 | 5972 |  | 3189.5
R-422A | HFC-134a 1,1,1,2-Tetrafluoroethane 11.5%; HFC-125 Pentafluoroethane 85.1%; Isobutane 3.4% |  | 3143.052 | 5844.402 |  | 3143.052
R-422B | HFC-134a 1,1,1,2-Tetrafluoroethane 42%; HFC-125 Pentafluoroethane 55%; Isobutane 3% |  | 2525.69 | 5101.19 |  | 2525.69
R-422C | HFC-125 Pentafluoroethane 82%; HFC-134a 1,1,1,2-Tetrafluoroethane 15%; Isobutane R-600a 3% |  | 3084.59 | 5781.59 |  | 3084.59
R-422D | HFC-125 Pentafluoroethane 65.1%; HFC-134a 1,1,1,2-Tetrafluoroethane 31.5%; Isobutane 3.4% |  | 2729.052 | 5340.402 |  | 2729.052
R-423A | HFC-134a 1,1,1,2-Tetrafluoroethane 52.5%; HFC-227ea 1,1,1,2,3,3,3-Heptafluoropropane 47.5% |  | 2280.25 | 4533 |  | 2280.25
R-424A | HFC-125 Pentafluoroethane 50.5%; HFC-134a 1,1,1,2-Tetrafluoroethane 47.0%; Butane (R-600) 1.0% Isobutane (R-600a) 0.9% Isopentane (R-601a) 0.6% |  | 2439.6161 | 5006.8661 |  | 2439.6161
R-426A | HFC-125 Pentafluoroethane 5.1%; HFC-134a 1,1,1,2-Tetrafluoroethane 93.0%; Butane (R-600) 1.3% Isobutane (R-600a) 0.6% |  | 1508.47 | 3885.82 |  | 1508.47
R-427A | HFC-32 Difluoromethane 15%; HFC-125 Pentafluoroethane 25%; HFC-134a 1,1,1,2-Tetrafluoroethane 50%; HFC-143a 1,1,1-Trifluoroethane 10% |  | 2138.25 | 4441 |  | 2138.25
R-428A | HFC-125 Pentafluoroethane 77.5%; HFC-143a 1,1,1-Trifluoroethane 20.0%; Propane (R-290) 0.6%; Isobutane (R-600a) 1.9% |  | 3607.3598 | 6100.1098 |  | 3607.3598
R-434A | HFC-125 Pentafluoroethane 63.2%; HFC-143a 1,1,1-Trifluoroethane 18%; HFC-134a 1,1,1,2-Tetrafluoroethane 16%; Isobutane (R-600a) 2.8% |  | 3245.484 | 5686.284 |  | 3245.484
R-436A | Hydrocarbon blend of 54% propane (R-290), 46% isobutane (R-600a) |  | 5 | 5 |  | 5
R-437A | HFC-125 Pentafluoroethane 19.5%; HFC-134a 1,1,1,2-Tetrafluoroethane 78.5%; Butane (R-600) 1.4%; Pentane (R-601) 0.6% |  | 1805.164 | 4244.914 |  | 1805.164
R-438A | HFC-125 Pentafluoroethane 45%; HFC-134a 1,1,1,2-Tetrafluoroethane 44.2%; HFC-32 Difluoromethane 8.5%; IsoButane (R-600a) 1.7%; Isopentane (R-601) 0.6% |  | 2237.98 | 4659.23 |  | 2237.98
R-441A | Hydrocarbon blend of 3.1% ethane (R-170); 54.8% propane (R-290), 36.1% n-Butane (R-600), and 6.0% isobutane (R-660a) |  | 5 | 5 |  | 5
R-442A | HFC-32 Difluoromethane 31%; HFC-125 Pentafluoroethane 31%; HFC-134a 1,1,1,2-Tetrafluoroethane 30%; HFC-152a 1,1-Difluoroethane 3%; HFC-227ea 1,1,1,2,3,3,3-Heptafluoropropane 5% |  | 1887.97 | 4118.41 |  | 1887.97
R-443A | Propane, isobutane, butane > 75%, hydrocarbon blend (Unacceptable for AC, SNAP list) |  | Not Available | Not Available |  | Not Available
R-444A | HFC-32 Difluoromethane 12%; HFC-152a 1,1-Difluoroethane 5%; R-1234ze HFO-1234ze(E) 83% | no MSDS yet | 88.03 | 302.28 |  | 88.03
R-444B | HFC-32 Difluoromethane 41.5%; R-152a 1,1-Difluoroethane 10%; R-1234ze HFO-1234ze 48.5% | no MSDS yet | 293.01 | 1011.135 |  | 293.01
R-445A | HFC-134a 1,1,1,2-Tetrafluoroethane 9%; R-744 CO2 6%; R-1234ze HFO-1234ze 85% | no MSDS yet | 129.61 | 345.61 |  | 129.61
R-446A | HFC-32 Difluoromethane 68%; R-1234ze HFO-1234ze 29%; R-600a isobutane 3% | no MSDS yet | 459.38 | 1584.78 |  | 459.38
R-447A | HFC-32 Difluoromethane 68%; HFC-125 Pentafluoroethane 3.5%; R-1234ze HFO-1234ze(E) 28.5% | no MSDS yet | 600 | Not Available |  | 600
R-447B | HFC-32 Difluoromethane 68%; R-1234ze HFO-1234ze(E) 24%; HFC-125 Pentafluoroethane 8% |  | 739.24 | 2092.64 |  | 739.24
R-448A | HFC-32 Difluoromethane 26%; HFC-125 Pentafluoroethane 26%; HFC-134a 1,1,1,2-Tetrafluoroethane 21%; R-1234yf HFO-1234yf 2,3,3,3-Tetrafluoropropene 20%; R-1234ze HFO-1234ze 7% |  | 1386.07 | 3061.37 |  | 1386.07
R-449A | HFC-32 Difluoromethane 24.3%; HFC-125 Pentafluoroethane 24.7%; HFC-134a 1,1,1,2-Tetrafluoroethane 25.7%; R-1234yf HFO-1234yf 2,3,3,3-Tetrafluoropropene 25.3% |  | 1396.288 | 3119.203 |  | 1396.288
R-449B | HFC-32 Difluoromethane 25.2%; HFC-125 Pentafluoroethane 24.3%; HFC-134a 1,1,1,2-Tetrafluoroethane 27.3%; R-1234yf HFO-1234yf 2,3,3,3-Tetrafluoropropene 23.2% |  | 1411.222 | 3176.032 |  | 1411.222
R-450A | HFC-134a 1,1,1,2-Tetrafluoroethane 42%; R-1234ze HFO-1234ze 58% |  | 601.18 | Not Available |  | 601.18
R-451A | HFC-134a 1,1,1,2-Tetrafluoroethane 10.2%; R-1234ze HFO-1234ze 89.8% |  | 146.758 | Not Available |  | 146.758
R-451B | HFC-134a 1,1,1,2-Tetrafluoroethane 11.2%; R-1234ze HFO-1234ze 88.8% |  | 161.048 | Not Available |  | 161.048
R-452A | HFC-32 Difluoromethane 11% HFC-125 Pentafluoroethane 59%; HFO-1234yf 2,3,3,3-Tetrafluoropropene 30% |  | 2139.55 | 4003.1 |  | 2139.55
R-452B | HFC-32 Difluoromethane 67% HFC-125 Pentafluoroethane 7%; HFO-1234yf 2,3,3,3-Tetrafluoropropene 26% |  | 697.51 | 2005.86 |  | 697.51
R-452C | HFC-32 Difluoromethane 12.5% HFC-125 Pentafluoroethane 61.0%; HFO-1234yf 2,3,3,3-Tetrafluoropropene 26.5% |  | 2219.64 | 4165.015 |  | 2219.64
R-453A | HFC-32 Difluoromethane 20%; HFC-125 Pentafluoroethane 20%; HFC-134a 1,1,1,2-Tetrafluoroethane (norflurane on MSDS) 53.8%; HFC-227ea 1,1,1,2,3,3,3-Heptafluoropropane 5%; R-600 Butane 0.6%; R-600a Isobutane 0.6% |  | 1765.388 | 4062.088 |  | 1765.388
R-454A | HFC-32 Difluoromethane 35%; HFO-1234yf 2,3,3,3-Tetrafluoropropene 65% |  | 239 | 816.15 |  | 239
R-454B | HFC-32 Difluoromethane 68.9%; HFO-1234yf 2,3,3,3-Tetrafluoropropene 31.1% |  | 466 | 1605.681 |  | 466
R-454C | HFO-1234yf 2,3,3,3-Tetrafluoropropene 78.5%; HFC-32 Difluoromethane 21.5% |  | 145.91 | 501.735 |  | 145.91
R-455A | HFC-32 Difluoromethane 21.5%; HFO-1234yf 2,3,3,3-Tetrafluoropropene 75.5%; R-744 CO2 3.0% |  | 145.91 | 501.735 |  | 145.91
R-456A | HFO-1234ze(E) 49%; HFC-134a 1,1,1,2-Tetrafluoroethane 45%; HFC-32 Difluoromethane 6% |  | 684.49 | 1863.79 |  | 684.49
R-457A | HFO-1234yf 2,3,3,3-Tetrafluoropropene 70.0%; HFC-32 Difluoromethane 18.0%; HFC-152a 1,1-Difluoroethane 12.0% |  | 137.08 | 472.54 |  | 137.08
R-458A | See also Tdx 20 by Bluon. HFC-134a - 61.4%; HFC-32 - 20.5%; HFC-227ea - 13.5%; HFC-125 - 4.0%; HFC-236fa - 0.6% |  | 1649.955 | 3848.72 |  | 1649.955
R-461A | HFC-125 Pentafluoroethane 55%; HFC-134a 1,1,1,2-Tetrafluoroethane 32%; HFC-143a 1,1,1-Trifluoroethane 5%; HFC-227ea 1,1,1,2,3,3,3-Heptafluoropropane 5%; R-600a isobutane 3% |  | 2767.19 | 5278.19 |  | 2767.19
R-462A | HFC-134a 1,1,1,2-Tetrafluoroethane 44%; HFC-125 Pentafluoroethane 42%; HFC-32 Difluoromethane 9%; R-600a isobutane 3%; HFC-143a 1,1,1-Trifluoroethane 2% |  | 2249.44 | 4679.79 |  | 2249.44
R-466A | HFC-32 Difluoromethane 49%; HFC-125 Pentafluoroethane 11.5%; CF3I (trifluoroiodide) 39.5% | 5.787 | 733 | 1872.345 |  | 733
R-500 | CFC-12 Dichlorodifluoromethane (73.8%); HFC-152a 1,1, Difluoroethane (26.2%) |  | 8076.688 | 8232.494 |  | 8076.688
R-502 | HCFC-22 Monochlorodifluoromethane 48.8%; CFC-115 Monochloropentafluoroethane 51.2% | 12 years (R-22); 7100 years (R-115) | 4656.72 | 5236.8 |  | 4656.72
R-503 | CFC-13 Chlorotrifluoromethane 60% HFC-23 Trifluoromethane 40% |  | 14560 | 11280 |  | 14560
R-507 | HFC-125 Pentafluoroethane 50%; HFC-143a 1,1,1-Trifluoroethane 50% | 29 years (R-125); 52 years (R-143a) | 3985 | 6120 |  | 3985
R-508A | HFC-23 Trifluoromethane 39% PFC-116 Hexafluoroethane 61% |  | 13214 | 9944.3 |  | 13214
R-508B | HFC-23 Trifluoromethane 46% PFC-116 Hexafluoroethane 54% |  | 13396 | 10180.2 |  | 13396
R-513A | HFO-1234yf 2,3,3,3-Tetrafluoropropene 56%; HFC-134a 1,1,1,2-Tetrafluoroethane 44% |  | 629.76 | 1685.76 |  | 629.76
R-514A | HFO 1336mzz(Z) - 74.7%; Trans-1,2-dichloroethylene (t-DCE) - 25.3% |  | 2 | 2 |  | 2
R-515A | R-1234ze(E) HFO 88%; HFC-227ea heptafluoropropane - 12% |  | 387.28 | 638.08 |  | 387.28
R-516A | HFO-1234yf 2,3,3,3-Tetrafluoropropene 77.5%; HFC-152a, 1,1-Difluoroethane 14%; HFC-134a 1,1,1,2-Tetrafluoroethane 8.5% |  | 139.685 | 387.505 |  | 139.685
SP34E | HFC-134a 1,1,1,2-Tetrafluoroethane > 96%; Butane (R-600) C5H10 < 3.9% Additive < 0.1% |  | 1372.96 | 3676.96 |  | 1372.96
TDX20 see also R-458A | TDX20 from Bluon Energy; see also R-458A |  | 1650 | Not Available |  | 1650
THR-03 | THR-03, also THR03 |  | 954 | Not Available |  | 954
DR-3 | DR-3 is "developmental refrigerant" 3, and is pre-commercial as of May 2016 |  | 148 | Not Available |  | 148
2-BTP | 2-bromotrifluoropropene (C3H2BrF3) (BTP) fire suppressant | 0.02 | 0.005 | 0.005 |  | 0.005
User Specified |  |  |  |  | User must specify refrigerant GWP on the Dashboard sheet. Note that the California Air Resources Board maintains a list of common refrigerants available at: https://ww2.arb.ca.gov/resources/documents/high-gwp-refrigerants
Sources:
1) http://www.ipcc.ch/pdf/assessment-report/ar4/wg1/ar4-wg1-chapter2.pdf (see Table 2.14 for GWP values)
2) http://www.epa.gov/climatechange/emissions/downloads/ghg_gwp.pdf (not a primary source for GWPs)
3) http://www.grida.no/climate/ipcc_tar/wg1/130.htm#tab41a
Note on A1: Gabe Mantegna: This tab copied from ACC.

## Change Log
Model Version | Date | Tab | First Cell
2022 v1a | 2022-05-17 | Dashboard | D19 | Updated user dashboard to have an input for measure type
Added input dashboard columns for both new and existing devices in the measure and counterfactual
|  |  | D34 | Added cells showing device retirement year and number of years of early retirement
|  |  | D41 | Updated dropdown to include user-specified refrigerant
Added cells for user to input GWP for a user-specified refrigerant
|  |  | C45 | Added cells showing measure start and end years
|  |  | E61 | Added intermediate calculations for new and existing devices
|  |  | C64 | Added intermediate calculations showing the percentage of device lifetime occuring during measure years and the percentage of device lifetime retired early
|  |  | B76 | Updated calculations to calculate PV cost streams from annual refrigerant leakage and end-of-life leakage from all relevant devices
Discounting is applied at the mid year (starting 0.5 years after the beginning of the measure start year)
|  |  | E113 | Added a table showing the total NPV cost for the measure and counterfactual case, and the breakdown by leakage type
|  | ACC Inputs | B6 | Added a list of measure types for dashboard dropdown
|  | Refrigerant Leakage | A41 | Added row for "no device" with 0 refrigerant leakage
|  | Refrigerant GWP | A155 | Added row for user-specified refrigerant with a note that the user should specify the GWP on the dashboard
|  | Dashboard | B6 | Updated text description of the calculator to reflect changes
| 2022-06-02 | ACC Inputs | E7 | Updated Nominal After-tax WACC to most recent values
|  | ACC Inputs | D4 | Upated GHG Adder costs to align with updated 2022 ACC Electric Model
|  | Refrigerant GWPs | A157 | Added a clarifying note on where to find the listed GWP values in the primary source
|  | Refrigerant GWPs |  | Filled in empty cells with text denoting "Not Available" where refrigerant GWPs were not available from the sources listed
2022 v1b | 2022-07-18 | Dashboard | E95 | Corrected the dollar year mistake that was in v1a by replacing the year 2022 with 2020 in the cost calculations that are supposed to reflect values in 2020$
|  | ACC inputs | D4 | Updated the GHG value to align with the GHG Value from Natural Gas ACC